## Pump Calcs
| Data Input |  | Catalog & Design Results |  | Required Data | Field Test Results |  | Required Data
Catalog & Design Data
1 | Design Point Flow (GPM) | 1800 | Specific Speed | 2206.4723 | 2, 4, 15 | Gauge Pressure in Feet | 101.64 | 19
2 | BEP Flow (GPM) | 2000 | Suction Specific Speed (US) | 14314.8731 | 2, 7, 13, 15 | Suction Velocity (fps) | 6.8083 | 21, 24
3 | Design Point Head (ft) | 121 | Suction Specific Speed (SI)) | 277.2051 | 2, 7, 13, 15 | Suction Velocity Head (ft) | 0.71977 | 21, 24
4 | BEP Head (ft) | 121 | Suction Energy | 185520755.6068 | 2, 7, 12, 13, 14, 15 | Discharge Velocity (fps) | 15.3187 | 21, 23
5 | Design Point Efficiency | 80% | NPSH Margin (BEP) | 2.2 | 7, 8 | Discharge Velocity Head (ft) | 3.6439 | 21, 23
6 | BEP Efficiency | 85% | Design Point Discharge Head | 126 | 3, 9 | Total Discharge Head (ft) | 107.5641 | 19 - 23
7 | BEP NPSHr (ft) | 10 | BEP Discharge Head | 126 | 4, 9 | Pump Water HP | 16.2976 | 19 - 23
8 | System NPSHa (ft) | 22 | Minimum Acceptable Flow* | 1689.7018 | 2, 7, 13, 15 | Motor BHP | 25.4635 | 25 - 28
9 | Suction Head + or - (ft) | 5 | Minimum Preferred Flow* | 1923.036 | 2, 7, 13, 15 | Pump Efficiency | 64% | 19 - 28
10 | Impeller Diameter (in) | 10 | Maximum Acceptable Flow* | 2133.1842 | 2, 7, 13, 15
11 | Impeller Trim Diameter (in) | 9 | Maximum Preferred Flow* | 2049.5875 | 2, 7, 13, 15
12 | Eye Diameter (in) | 7.2 | Trimmed Impeller Flow % | 90% | 10, 11
13 | Number of Eyes (1 or 2) | 1 | Trimmed Impeller Head % | 81% | 10, 11
14 | Liquid Specific Gravity | 1 | Higher / Lower RPM Flow % | 94.44% | 15, 16
15 | Pump Speed (RPM) | 1800 | Higher / Lower RPM Head % | 89.2% | 15, 16
16 | Higher / Lower Speed (RPM) | 1700 | Design Point HP | 68.75 | 1, 3, 5, 14
17 | Motor Efficiency | 93% | BEP HP | 71.8954 | 2, 4, 6, 14
18 | Power Cost / KWH (decimal) | 0.1 | Design Point Wire / Water Eff | 74.4% | 5, 17
| Pump Field Test Data |  | BEP Wire / Water Eff | 79.05% | 6, 17
19 | Discharge Gauge Pressure (PSI) | 44 | Design Point kW / 1000 Gallons | 0.51063 | 1, 3, 5, 14, 17
20 | Gauge Elevation Above Suction (ft) | 3 | BEP kW / 1000 Gallons | 0.48059 | 2, 4, 6, 14, 17
21 | Pump Flow | 600 | Design Point $$ / 1000 Gallons | 0.051063 | 1, 3, 5, 14, 17, 18
22 | Liquid Specific Gravity | 1 | BEP $$ / 1000 Gallons | 0.048059 | 2, 4, 6, 14, 17, 10
23 | Pipe ID At Gauge (in) | 4
24 | Suction Pipe ID (in) | 6 | Enter the catalog or design data in yellow cells F3 - F20 (1 - 18). Enter field test data in cells F22 - F31 (19 - 28).
25 | Motor Voltage (Ave) | 460 | Catalog and design calculations will appear in cells K3 - K25. The blue numbers to the right of these cells are
26 | Motor Amps (Ave) | 33 | the data required for the calculations (the blue numbers in column A). If required data is not entered the
27 | Motor PF | 85% | resulting calculation will be incorrect. Field test calculations will appear in cells S3 - S11. The blue numbers
28 | Motor Efficiency | 85% | to the right of these cells are the data required for the calculations (the blue numbers in column A). If any
required data in not entered the resulting calculation will be incorrect.
* Based on Suction Specific Speed. See reference below.
http://www.lawrencepumps.com/Newsletter/news_v03_i2_Feb06.html
www.PumpTechnw.com

## AC Power & Motor Calcs
| Data Input |  | Calculated Results |  |  | Required Data | Calculated Test Results |  | Required Data
Catalog & Design Data
1 | Motor HP | 5 | Motor HP (From Torque) |  | 5.0286 | 4, 5 | Average Voltage | 467 | 13 - 15
2 | Motor RPM | 1760 | Motor Torque (From HP) |  | 14.9148 | 1, 2 | Voltage Deviation P1 | 12 | 13 - 15 | 12
3 | Motor Torque | 15 | Motor HP (Single Phase) |  | 4.898 | 4, 6, 8, 9 | Voltage Deviation P2 | 5 | 13 - 15 | 5
4 | Motor Voltage (Single Phase) | 230 | Available HP (+ SF) |  | 5.6327 | 4, 6, 8, 9, 10 | Voltage Deviation P3 | 17 | 13 - 15 | -17
5 | Motor Voltage (Three Phase) | 230 | Motor HP ( Three Phase) |  | 2.6258 | 5, 7, 8, 9 | Voltage Unbalance | 3.64% | 13 - 15 | 12
6 | Motor Amps (Single Phase) | 21 | Available HP (+ SF) |  | 3.0197 | 5, 7, 8, 9, 10 | Average Current | 52.6667 | 16 - 18 | 17
7 | Motor Amps (Three Phase) | 6.5 | Motor Torque (Single Phase) |  | 14.6105 | 2, 4, 6, 8, 9 | Current Deviation P1 | 6.6667 | 16 - 18 | -6.6667
8 | Motor Efficiency | 89% | Motor Torque (Three Phase) |  | 7.8326 | 2, 5, 7, 8, 9 | Current Deviation P2 | 1.3333 | 16 - 18 | 1.3333
9 | Motor Power Factor (dec) | 0.85 | Motor kVA (Single Phase) |  | 4.83 | 4, 6 | Current Deviation P3 | 5.3333 | 16 - 18 | 5.3333
10 | Motor Service Factor (dec) | 1.15 | Motor kVA (Three Phase) |  | 2.5744 | 5, 7 | Current Unbalance | 12.66% | 16 - 18 | 6.6667
11 | Motor Temp Rise (⁰C) |  | Motor kW (Single Phase) |  | 4.1055 | 4, 6, 9 | Motor kVA | 42.5991 | 13 - 18 | 6.6667
12 | Power Cost / kWH | 0.1 | Motor kW (Three Phase) |  | 2.2009 | 5, 7, 9 | Motor kW | 36.2092 | 13 - 19
| Motor Field Test Data |  | $$ / Hour (Single Phase) |  | 0.41055 | 4, 6, 9, 12 | Motor HP | 43.6841 | 13 - 20
13 | Motor Voltage (P1) | 479 | $$ / Hour (Three Phase) |  | 0.22009 | 5, 7, 9, 12 | $$ / Hour | 3.6209 | 13 - 20
14 | Motor Voltage (P2) | 472
15 | Motor Voltage (P3) | 450
16 | Motor Amps (P1) | 46 |  | Enter the catalog or design data in yellow cells E3 - E20 (1 - 14). Enter field test data in cells E16 - E23 (13 -20).
17 | Motor Amps (P2) | 54 |  | Catalog and design calculations will appear in cells J3 - J16. The blue numbers to the right of these cells are
18 | Motor Amps (P3) | 58 |  | the data required for the calculations (the blue numbers in column A). If required data is not entered the
19 | Motor Power Factor (dec) | 0.85 |  | resulting calculation will be incorrect. Field test calculations will appear in cells R3 - R16. The blue numbers
20 | Motor Efficiency | 90% |  | to the right of these cells are the data required for the calculations (the blue numbers in column A). If any
required data in not entered the resulting calculation will be incorrect.

## Simple Pipe Calcs
| Data Input (Water 60⁰ F) |  | Calculated Data |  | Hazen & Williams C Values
| Pipe Segment 1 |  | Pipe Segment 1 |  | Pipe Type | C Range | C Average | Commonly Used
1 | Flow Rate (GPM) | 1400 | Velocity in Ft/sec | 8.9359 | Cast / Ductile Iron - New | 150 - 80 | 130 | 100
2 | Pipe ID (Inches) | 8 | Velocity Head in Ft | 1.2399 | Cast Iron 10 years old | 113 - 107
3 | Pipe Length (Feet) | 100 | Friction / 100 Feet of Pipe | 3.4699 | Cast Iron 20 years old | 100 - 89
4 | Hazen & Williams C Value | 130 | Segment 1 Friction | 3.4699 | Cast Iron 30 years old | 75 - 90
| Pipe Segment 2 |  | Reynolds Number | 553727.8775 | Cast Iron 40 years old | 83 - 64
5 | Flow Rate (GPM) | 900 | Pipe Segment 2 |  | Tar Coated Cast Iron | 145 - 50 | 130 | 100
6 | Pipe ID (Inches) | 6 | Velocity in Ft/sec | 10.2125 | Steel - New | 150 - 80 | 130 | 100
7 | Pipe Length (Feet) | 1000 | Velocity Head in Ft | 1.6195 | Corrugated Steel |  | 60 | 60
8 | Hazen & Williams C Value | 130 | Friction / 100 Feet of Pipe | 6.2062 | Cement Lined Iron / Steel | 160 - 130 | 148 | 140
| Pipe Segment 3 |  | Segment 2 Friction | 62.0624 | Asphalt Lined Iron / Steel | 140 - 130
9 | Flow Rate (GPM) | 500 | Total Friction Losses 1 & 2 | 65.5322 | Copper, Brass, Lead, Glass | 150 - 120 | 140 | 130
10 | Pipe ID (Inches) | 5 | Reynolds Number | 474623.895 | Aluminum | 150 - 130
11 | Pipe Length (Feet) | 1000 | Pipe Segment 3 |  | Concrete | 152 - 85 | 120 | 100
12 | Hazen & Williams C Value | 130 | Velocity in Ft/sec | 8.17 | Asbestos Cement | 140
|  |  | Velocity Head in Ft | 1.0365 | PVC | 160 - 150 | 155 | 150
|  |  | Friction / 100 Feet of Pipe | 5.0736 | PE | 140
|  |  | Segment 3 Friction | 50.7364
|  |  | Total Friction Losses 1, 2 & 3 | 116.2687
|  |  | Reynolds Number | 316415.93 | Piping segments can be in series or branch nodes. The example shows the results when
segments 2 and 3 branch off segment 1.
For a more comprehensive calculator, download my Pipe & Fittings Calculator.