## Sheet1
SIMPLE WASTEWATER PUMP DRAW DOWN CALCULATOR
Vertical Partitioned Wet / Dry Well
INPUT DATA
Well Diameter (inches) | 96 | 4 | convert inches to feet & radius
Fill Distance (inches) see below | 36 | 3 | convert inches to feet
Pump Down Distance (inches) | 12 | 1 | convert inches to feet
Pump Down Time (seconds) | 40 | 0.66667 | convert seconds to minutes
Discharge Gauge Pressure (PSI) | 25 | 57.75 | convert PSI to feet
Gauge Location to Water Level (inches) | 108 | 9 | convert inches to feet
Discharge Pipe ID @ Gauge (inches) | 4 |  | convert inches to feet
CALCULATED RESULTS
Wet Pit Volume / Foot (Gal) | 128.7822 | 128.7822
Draw Down Volume (Gal) | 128.7822
Flow Rate (GPM) | 193.1733
Discharge Velocity @ Gauge (ft/sec) | 4.932
Discharge Velocity Head (ft) | 0.3777
TDH (ft) | 67.1277
TDH (PSI) | 29.0596
Notes
The fill distance is the distance from the wet / dry partition to the wet well wall at the well diameter.
Enter vertical distance from the Pump On Water Level to discharge gauge location in cell C11. If the water level is above the gauge, enter a negative number.
Calculations ignore discharge pipe friction since pipe length is usually short. Calculate manually and subtract if necessary.
Use a calibrated gauge that reads the measured pressure near the mid point of the gauge range.