## Data Input
IMPELLER HERTZ CALCULATOR
1) Enter the pump test curve frequency in Hertz in cell B17
2) Enter the reduced or increased frequency in Hertz in cell B21
3) Enter up to eight flow values in cells C17 - J17
If there are fewer than eight points enter the last flow multiple times
4) Enter the corresponding heads in cells K17 - R17
If there are fewer than eight points enter the last head multiple times
5) Enter the flow efficiencies (%) in cells C18 - J18
If there are fewer than eight points enter the last efficiency multiple times
6) Calculated flows, heads & BHP will appear in the blue cells
7) Click on the tabs to view the curves
| Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
50 | 250 | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000 | 205 | 201 | 195 | 188 | 178 | 165 | 147 | 125
Pump Eff | Q1: 50; Q2: 60; Q3: 73; Q4: 80; Q5: 84; Q6: 86; Q7: 86; Q8: 83
BHP | Q1: 25.8838; Q2: 42.298; Q3: 50.5915; Q4: 59.3434; Q5: 66.8891; Q6: 72.6744; Q7: 75.5374; Q8: 76.0618
60 | 300 | 600 | 900 | 1200 | 1500 | 1800 | 2100 | 2400 | 295.2 | 289.44 | 280.8 | 270.72 | 256.32 | 237.6 | 211.68 | 180
BHP | Q1: 44.7273; Q2: 73.0909; Q3: 87.4222; Q4: 102.5455; Q5: 115.5844; Q6: 125.5814; Q7: 130.5285; Q8: 131.4348
1.2
1.44