## Data Input
PULLEY SIZE CALCULATOR
1) Enter the motor RPM in cell E16
2) Enter the motor pulley diameter (in inches) in cell E17
3) Enter the pump pulley diameter (in inches) in cell E18
4) Enter up to eight test curve flow values at motor RPM in cells C21 - J21
If there are fewer than eight points enter the last flow multiple times
5) Enter the corresponding heads in cells K21 - R21
If there are fewer than eight points enter the last head multiple times
6) Enter the flow efficiencies (%) in cells C22 - J22
If there are fewer than eight points enter the last efficiency multiple times
7) Calculated RPM, flows, heads & BHP will appear in the blue cells
8) Click on the tabs to view the curves
Motor RPM |  |  | 1780
Motor Pulley Diameter |  |  | 4
Pump Pulley Diameter |  |  | 6
| Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
Q & H | 250 | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000 | 205 | 201 | 195 | 188 | 178 | 165 | 147 | 125
Pump Eff | Q1: 50; Q2: 60; 6 Q3: 73; 6 Q4: 80; 6 Q5: 84; 6 Q6: 86; 6 Q7: 86; 6 Q8: 83
BHP | Q1: 25.8838; Q2: 42.298; 6 Q3: 50.5915; 6 Q4: 59.3434; 6 Q5: 66.8891; 6 Q6: 72.6744; 6 Q7: 75.5374; 6 Q8: 76.0618
New RPM | Q1: 1186.6667
Q & H | 166.6667 | 333.3333 | 500 | 666.6667 | 833.3333 | 1000 | 1166.6667 | 1333.3333 | 91.1111 | 89.3333 | 86.6667 | 83.5556 | 79.1111 | 73.3333 | 65.3333 | 55.5556
BHP | Q1: 7.6693; Q2: 12.5327; 6 Q3: 14.9901; 6 Q4: 17.5832; 6 Q5: 19.819; 6 Q6: 21.5332; 6 Q7: 22.3814; 6 Q8: 22.5368
0.66667
0.44444
1186.6667