## VFPPA Data Input
[6 empty] | Variable Frequency Parallel Pump Analyzer (Beta) | [16 empty] | Average Efficiency Calculator
[6 empty] | Joe Evans, Ph.D 7/4/10 Customer Education PumpTech, Inc | [8 empty] | http://www.PumpEd101.com | [7 empty] | Pump 1 Full Speed Flow |  |  |  | 350
[23 empty] | Pump 1 Eff @ Full Speed Flow |  |  |  | 78%
[23 empty] | Pump 2 Flow @ Reduced Speed |  |  |  | 100
[6 empty] | Follow the five steps below to view the operation of two identical centrifugal pumps under VFD control. | [16 empty] | Pump 2 Eff @ Reduced Speed |  |  |  | 50%
Scroll down for more detailed instructions.
| AFFINITY LAW CALCULATOR | [21 empty] | Total Flow |  |  |  | 450
[23 empty] | % of Total Flow - Pump 1 |  |  |  | 77.78%
[6 empty] | 1) Enter the pump description in the yellow box to the right | [7 empty] | Vertical Multistage (25HP) | [8 empty] | % of Total Flow - Pump 2 |  |  |  | 22.22%
3.5
[23 empty] | Average Hydraulic Efficiency |  |  |  | 71.78%
| ENTER RPM IN CELL B22 |  |  |  |  | 2) Enter eight 60 hertz flows In Q1 - Q8 (Cells H20 - O20) | [16 empty] | Different Speeds
Enter the corresponding heads (in ft) in H1 - H8 (Cells P20 - W20)
[6 empty] | (*See instructions below when entering fewer than eight points) | [16 empty] | Energy Savings Calculator
[30 empty] | Parallel calcs | q1 | q2 | q3 | q4 | q5 | q6 | q7 | q8 | h1 | h2 | h3 | h4 | h5 | h6 | h7 | h8
[6 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8 |  | Pump Eff @ Synchronous Speed |  |  |  | 66%
60 | 3600 | 100% | 100% | 100% |  | 50 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 280 | 271 | 262 | 252 | 240 | 225 | 206 | 182 |  | Motor Efficiency |  |  |  | 90% |  |  | 60hz | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800 | 280 | 271 | 262 | 252 | 240 | 225 | 206 | 182
[23 empty] | Cost / KWh |  |  |  | 0.1
[6 empty] | 3) To plot a system curve (static), enter the head (in ft) | [7 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
[6 empty] | in SH1 - SH8 (Cells P62 - W62). (See instructions below) | [7 empty] | 206 | 206 | 206 | 206 | 206 | 206 | 206 | 206 |  | BHP Synchronous Speed |  |  |  | 35.4683
[23 empty] | Cost / Hr Synchronous Speed |  |  |  | 2.9399
[6 empty] | 4) Enter the pump's hydraulic efficiencies in Ef 1 - Ef 8 | [7 empty] | Ef 1 | Ef 2 | Ef 3 | Ef 4 | Ef 5 | Ef 6 | Ef 7 | Ef 8 |  | BHP Different Speeds |  |  |  | 32.6133
[6 empty] | (Cells P67 - W67) that correspond to the flows in Q1 - Q8 | [7 empty] | 25% | 45% | 55% | 60% | 67% | 72% | 78% | 76% |  | Cost / Hr Different Speeds |  |  |  | 2.7033
Enter as a decimal equivalent. (See instructions below)
Scroll down to row 112 for more detailed instructions
[6 empty] | 5) Click on the various tabs to view pump performance. | [16 empty] | and an explaination of the example provided.
| AFFINITY LAW CALCULATOR | [5 empty] | VFPPA Instructions
The Variable Frequency Parallel Pump Analyzer allows you to compare single pump and parallel pump operation at
various frequencies. The "Two Pumps" tab shows both pumps operating at the same speed.
Step 1
Enter the pump description as you would like it to appear on the chart.
Step 2
| Enter a motor speed for 60 Hz | [5 empty] | Auto Plot requires that you enter eight, 60 Hz operating points in the row with the yellow background. Flows are entered
| operation in the cell with the | [5 empty] | beneath Q1 - Q8 and the corresponding heads are entered beneath H1 - H8. It is not necessary to begin with shutoff head
| yellow background and motor | [5 empty] | unless the pump will operate to the far left of the curve. Corresponding flows and heads are calculated for each point from
| speeds at the lower frequencies | [5 empty] | 59 - 45 Hz, however, Auto Plot displays the curves in 5hz increments (i.e. 55, 50, 45, etc). The labels displayed at each
| will be displayed. Note that the | [5 empty] | xy intercept on the head / capacity curves is the hydraulic efficiency at that point. *If you wish to enter fewer than eight points,
enter the last point multiple times. For example if you have only six points, enter the data in Q6/H6 again in both Q7/H7
and Q8/H8. The same will hold true for Steps 3 & 4.
Step 3
The system curve represents static head only. Enter the same value in each field.
Step 4
Enter the pump's hydraulic efficiency for each single pump flow point as a decimal equivalent.
Step 5
Click on the "One Pump" Tab to view the performance of a single pump at various speeds. If needed, you can insert an
angled line (see example) to show where the effeciency isomer crosses the system curve. Click on the "Two Pumps"
curve for two pumps running at various synchronous speeds. The other tabs show both sets of curves over various
frequency ranges. The 45-60 Hz tab is usually pretty busy so use the others for detained study.
Average Efficiency Calculator Instructions
The Efficiency Calculator allows you to compare the efficiency of two pumps operating at synchronous speeds to two pumps
operating at different speeds (one at full speed and one at a lower speed). The "Two Pumps" tab shows the efficiency of
two pumps operating at the same speed at various flows and speeds. In the example provided the angled line indicates
an efficiency of about 66% at 450 GPM. The frequency at this point is between 54 & 55 Hz. To compare this with two pumps
operating at different speeds (one at full speed and one at a lower speed) click on the "One Pump" tab. The 60 Hz curve shows
a full speed flow of 350 GPM at an efficiency of 78%. This data was entered into cells AE5 & AE6 of the Efficiency calculator.
An additional 100 GPM is needed to match the total flow of the synchronous speed pumps. The angled line indicates that
this volume can be added by the second pump running between 52 & 53 Hz at an efficiency of about 50%. This data was entered
into cells AE7 & AE8 of the calculator. The calculator then calculates the total flow, the % contribution of each pump and the
average efficiency of the two pump operating at different speeds. Use this proceedure to evaluate any flow combination.
The calculator shows that the pumps used in the example operate at a higher efficiency when running independently
than when running synchronously.
Energy Savings Calculator Instructions
Enter the Synchronous Speed efficiency at the flow point in cell AE19. The red angled line, in the two pump tab, shows
a flow of 450 GPM at an efficiency of about 66%. Enter the motor efficiency and the power cost per KWh in cells AE20 and AE62.
The calculator calculates the BHP and cost per hour of operation for both control methods.
Use With Three or More Pumps
You can also use the calculator to evaluate three or more pumps. When evaluating three pumps enter the combined flow and
efficiency of two pumps running at full speed in AE5 & AE6. Enter the reduced flow and efficiency of the third pump in
AE7 & AE8.
http://www.pumped101.com
59 | 3540 | 98.33% | 96.69% | 95.08% | 59 | 48.3472 | 98.3333 | 147.5 | 196.6667 | 245.8333 | 295 | 344.1667 | 393.3333 | 270.7444 | 262.0419 | 253.3394 | 243.67 | 232.0667 | 217.5625 | 199.1906 | 175.9839 | [8 empty] | 55hz | 84.0278 | 183.3333 | 275 | 366.6667 | 458.3333 | 550 | 641.6667 | 733.3333 | 235.2778 | 227.7153 | 220.1528 | 211.75 | 201.6667 | 189.0625 | 173.0972 | 152.9306
58 | 3480 | 96.67% | 93.44% | 90.33% | 58 | 46.7222 | 96.6667 | 145 | 193.3333 | 241.6667 | 290 | 338.3333 | 386.6667 | 261.6444 | 253.2344 | 244.8244 | 235.48 | 224.2667 | 210.25 | 192.4956 | 170.0689 | [8 empty] | 50hz | 69.4444 | 166.6667 | 250 | 333.3333 | 416.6667 | 500 | 583.3333 | 666.6667 | 194.4444 | 188.1944 | 181.9444 | 175 | 166.6667 | 156.25 | 143.0556 | 126.3889
57 | 3420 | 95% | 90.25% | 85.74% | 57 | 45.125 | 95 | 142.5 | 190 | 237.5 | 285 | 332.5 | 380 | 252.7 | 244.5775 | 236.455 | 227.43 | 216.6 | 203.0625 | 185.915 | 164.255 | [8 empty] | 45hz | 56.25 | 150 | 225 | 300 | 375 | 450 | 525 | 600 | 157.5 | 152.4375 | 147.375 | 141.75 | 135 | 126.5625 | 115.875 | 102.375
56 | 3360 | 93.33% | 87.11% | 81.3% | 56 | 43.5556 | 93.3333 | 140 | 186.6667 | 233.3333 | 280 | 326.6667 | 373.3333 | 243.9111 | 236.0711 | 228.2311 | 219.52 | 209.0667 | 196 | 179.4489 | 158.5422 | [8 empty] | 57hz | 90.25 | 190 | 285 | 380 | 475 | 570 | 665 | 760 | 252.7 | 244.5775 | 236.455 | 227.43 | 216.6 | 203.0625 | 185.915 | 164.255
55 | 3300 | 91.67% | 84.03% | 77.03% | 55 | 42.0139 | 91.6667 | 137.5 | 183.3333 | 229.1667 | 275 | 320.8333 | 366.6667 | 235.2778 | 227.7153 | 220.1528 | 211.75 | 201.6667 | 189.0625 | 173.0972 | 152.9306 | [8 empty] | 53hz | 34.0278 | 116.6667 | 175 | 233.3333 | 291.6667 | 350 | 408.3333 | 466.6667 | 95.2778 | 92.2153 | 89.1528 | 85.75 | 81.6667 | 76.5625 | 70.0972 | 61.9306
54 | 3240 | 90% | 81% | 72.9% | 54 | 40.5 | 90 | 135 | 180 | 225 | 270 | 315 | 360 | 226.8 | 219.51 | 212.22 | 204.12 | 194.4 | 182.25 | 166.86 | 147.42 | [8 empty] | 30hz | 25 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 70 | 67.75 | 65.5 | 63 | 60 | 56.25 | 51.5 | 45.5
53 | 3180 | 88.33% | 78.03% | 68.92% | 53 | 39.0139 | 88.3333 | 132.5 | 176.6667 | 220.8333 | 265 | 309.1667 | 353.3333 | 218.4778 | 211.4553 | 204.4328 | 196.63 | 187.2667 | 175.5625 | 160.7372 | 142.0106
52 | 3120 | 86.67% | 75.11% | 65.1% | 52 | 37.5556 | 86.6667 | 130 | 173.3333 | 216.6667 | 260 | 303.3333 | 346.6667 | 210.3111 | 203.5511 | 196.7911 | 189.28 | 180.2667 | 169 | 154.7289 | 136.7022
51 | 3060 | 85% | 72.25% | 61.41% | 51 | 36.125 | 85 | 127.5 | 170 | 212.5 | 255 | 297.5 | 340 | 202.3 | 195.7975 | 189.295 | 182.07 | 173.4 | 162.5625 | 148.835 | 131.495
50 | 3000 | 83.33% | 69.44% | 57.87% | 50 | 34.7222 | 83.3333 | 125 | 166.6667 | 208.3333 | 250 | 291.6667 | 333.3333 | 194.4444 | 188.1944 | 181.9444 | 175 | 166.6667 | 156.25 | 143.0556 | 126.3889
49 | 2940 | 81.67% | 66.69% | 54.47% | 49 | 33.3472 | 81.6667 | 122.5 | 163.3333 | 204.1667 | 245 | 285.8333 | 326.6667 | 186.7444 | 180.7419 | 174.7394 | 168.07 | 160.0667 | 150.0625 | 137.3906 | 121.3839
48 | 2880 | 80% | 64% | 51.2% | 48 | 32 | 80 | 120 | 160 | 200 | 240 | 280 | 320 | 179.2 | 173.44 | 167.68 | 161.28 | 153.6 | 144 | 131.84 | 116.48
47 | 2820 | 78.33% | 61.36% | 48.07% | 47 | 30.6806 | 78.3333 | 117.5 | 156.6667 | 195.8333 | 235 | 274.1667 | 313.3333 | 171.8111 | 166.2886 | 160.7661 | 154.63 | 147.2667 | 138.0625 | 126.4039 | 111.6772
46 | 2760 | 76.67% | 58.78% | 45.06% | 46 | 29.3889 | 76.6667 | 115 | 153.3333 | 191.6667 | 230 | 268.3333 | 306.6667 | 164.5778 | 159.2878 | 153.9978 | 148.12 | 141.0667 | 132.25 | 121.0822 | 106.9756
45 | 2700 | 75% | 56.25% | 42.19% | 45 | 28.125 | 75 | 112.5 | 150 | 187.5 | 225 | 262.5 | 300 | 157.5 | 152.4375 | 147.375 | 141.75 | 135 | 126.5625 | 115.875 | 102.375
44 | 2640 | 73.33% | 53.78% | 39.44% | 44 | 26.8889 | 73.3333 | 110 | 146.6667 | 183.3333 | 220 | 256.6667 | 293.3333 | 150.5778 | 145.7378 | 140.8978 | 135.52 | 129.0667 | 121 | 110.7822 | 97.8756
43 | 2580 | 71.67% | 51.36% | 36.81% | 43 | 25.6806 | 71.6667 | 107.5 | 143.3333 | 179.1667 | 215 | 250.8333 | 286.6667 | 143.8111 | 139.1886 | 134.5661 | 129.43 | 123.2667 | 115.5625 | 105.8039 | 93.4772
42 | 2520 | 70% | 49% | 34.3% | 42 | 24.5 | 70 | 105 | 140 | 175 | 210 | 245 | 280 | 137.2 | 132.79 | 128.38 | 123.48 | 117.6 | 110.25 | 100.94 | 89.18
41 | 2460 | 68.33% | 46.69% | 31.91% | 41 | 23.3472 | 68.3333 | 102.5 | 136.6667 | 170.8333 | 205 | 239.1667 | 273.3333 | 130.7444 | 126.5419 | 122.3394 | 117.67 | 112.0667 | 105.0625 | 96.1906 | 84.9839
40 | 2400 | 66.67% | 44.44% | 29.63% | 40 | 22.2222 | 66.6667 | 100 | 133.3333 | 166.6667 | 200 | 233.3333 | 266.6667 | 124.4444 | 120.4444 | 116.4444 | 112 | 106.6667 | 100 | 91.5556 | 80.8889
39 | 2340 | 65% | 42.25% | 27.46% | 39 | 21.125 | 65 | 97.5 | 130 | 162.5 | 195 | 227.5 | 260 | 118.3 | 114.4975 | 110.695 | 106.47 | 101.4 | 95.0625 | 87.035 | 76.895
38 | 2280 | 63.33% | 40.11% | 25.4% | 38 | 20.0556 | 63.3333 | 95 | 126.6667 | 158.3333 | 190 | 221.6667 | 253.3333 | 112.3111 | 108.7011 | 105.0911 | 101.08 | 96.2667 | 90.25 | 82.6289 | 73.0022
37 | 2220 | 61.67% | 38.03% | 23.45% | 37 | 19.0139 | 61.6667 | 92.5 | 123.3333 | 154.1667 | 185 | 215.8333 | 246.6667 | 106.4778 | 103.0553 | 99.6328 | 95.83 | 91.2667 | 85.5625 | 78.3372 | 69.2106
36 | 2160 | 60% | 36% | 21.6% | 36 | 18 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 100.8 | 97.56 | 94.32 | 90.72 | 86.4 | 81 | 74.16 | 65.52
35 | 2100 | 58.33% | 34.03% | 19.85% | 35 | 17.0139 | 58.3333 | 87.5 | 116.6667 | 145.8333 | 175 | 204.1667 | 233.3333 | 95.2778 | 92.2153 | 89.1528 | 85.75 | 81.6667 | 76.5625 | 70.0972 | 61.9306
34 | 2040 | 56.67% | 32.11% | 18.2% | 34 | 16.0556 | 56.6667 | 85 | 113.3333 | 141.6667 | 170 | 198.3333 | 226.6667 | 89.9111 | 87.0211 | 84.1311 | 80.92 | 77.0667 | 72.25 | 66.1489 | 58.4422
33 | 1980 | 55% | 30.25% | 16.64% | 33 | 15.125 | 55 | 82.5 | 110 | 137.5 | 165 | 192.5 | 220 | 84.7 | 81.9775 | 79.255 | 76.23 | 72.6 | 68.0625 | 62.315 | 55.055
32 | 1920 | 53.33% | 28.44% | 15.17% | 32 | 14.2222 | 53.3333 | 80 | 106.6667 | 133.3333 | 160 | 186.6667 | 213.3333 | 79.6444 | 77.0844 | 74.5244 | 71.68 | 68.2667 | 64 | 58.5956 | 51.7689
31 | 1860 | 51.67% | 26.69% | 13.79% | 31 | 13.3472 | 51.6667 | 77.5 | 103.3333 | 129.1667 | 155 | 180.8333 | 206.6667 | 74.7444 | 72.3419 | 69.9394 | 67.27 | 64.0667 | 60.0625 | 54.9906 | 48.5839
30 | 1800 | 50% | 25% | 12.5% | 30 | 12.5 | 50 | 75 | 100 | 125 | 150 | 175 | 200 | 70 | 67.75 | 65.5 | 63 | 60 | 56.25 | 51.5 | 45.5
[7 empty] | 100 | 77 | 58
[14 empty] | 121.2121 | 117.316 | 113.4199 | 109.0909 | 103.8961 | 97.4026 | 89.1775 | 78.7879
[14 empty] | 101.8519 | 98.578 | 95.3042 | 91.6667 | 87.3016 | 81.8452 | 74.9339 | 66.2037
[14 empty] | 84.1751 | 81.4695 | 78.7638 | 75.7576 | 72.1501 | 67.6407 | 61.9288 | 54.7138 | system head in psi
[14 empty] | 68.1818 | 65.9903 | 63.7987 | 61.3636 | 58.4416 | 54.789 | 50.1623 | 44.3182 | sh1 | sh2 | sh3 | sh4 | sh5 | sh6 | sh7 | sh8
[14 empty] | 53.8721 | 52.1405 | 50.4089 | 48.4848 | 46.176 | 43.29 | 39.6344 | 35.0168 | 89.1775 | 89.1775 | 89.1775 | 89.1775 | 89.1775 | 89.1775 | 89.1775 | 89.1775
[14 empty] | 41.2458 | 39.92 | 38.5943 | 37.1212 | 35.3535 | 33.1439 | 30.3451 | 26.8098
[14 empty] | 30.303 | 29.329 | 28.355 | 27.2727 | 25.974 | 24.3506 | 22.2944 | 19.697