## CPSA
Centrifugal Pump Selection Assistant with "Auto Plot"
Joe Evans, Ph.D 4/20/05
Follow the four steps below to view the potential power savings of a centrifugal pump operating under VFD control.
Scroll down to line 80 for more detailed instructions.
AFFINITY LAW CALCULATOR
[6 empty] | 1) Enter the pump description in the yellow box to the right | [7 empty] | Berkeley B6EXPBL 15.5" Trim 125 HP / 1800 RPM
| ENTER RPM IN CELL B22 |  |  |  |  | 2) Enter eight 60 hertz flows In Q1 - Q8 (Cells H20 - O20)
Enter the corresponding heads (in ft) in H1 - H8 (Cells P20 - W20)
(*See instructions below when entering fewer than eight points)
[6 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
60 | 3600 | 100% | 100% | 100% |  | 500 | 1000 | 1500 | 2000 | 2500 | 3000 | 3000 | 3000 | 225 | 220 | 210 | 187 | 152 | 100 | 100 | 100
59 | 3540 | 98.33% | 96.69% | 95.08% | 59 | 491.6667 | 983.3333 | 1475 | 1966.6667 | 2458.3333 | 2950 | 2950 | 2950 | 217.5625 | 212.7278 | 203.0583 | 180.8186 | 146.9756 | 96.6944 | 96.6944 | 96.6944 |  | HP Calculations | [6 empty] | PSI Calculations
58 | 3480 | 96.67% | 93.44% | 90.33% | 58 | 483.3333 | 966.6667 | 1450 | 1933.3333 | 2416.6667 | 2900 | 2900 | 2900 | 210.25 | 205.5778 | 196.2333 | 174.7411 | 142.0356 | 93.4444 | 93.4444 | 93.4444 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
57 | 3420 | 95% | 90.25% | 85.74% | 57 | 475 | 950 | 1425 | 1900 | 2375 | 2850 | 2850 | 2850 | 203.0625 | 198.55 | 189.525 | 168.7675 | 137.18 | 90.25 | 90.25 | 90.25 | #DIV/0! | 86.8056 | 106.0606 | 116.5981 | 119.9495 | 116.5501 | 116.5501 | 116.5501 | 97.4026 | 95.2381 | 90.9091 | 80.9524 | 65.8009 | 43.29 | 43.29 | 43.29
56 | 3360 | 93.33% | 87.11% | 81.3% | 56 | 466.6667 | 933.3333 | 1400 | 1866.6667 | 2333.3333 | 2800 | 2800 | 2800 | 196 | 191.6444 | 182.9333 | 162.8978 | 132.4089 | 87.1111 | 87.1111 | 87.1111
55 | 3300 | 91.67% | 84.03% | 77.03% | 55 | 458.3333 | 916.6667 | 1375 | 1833.3333 | 2291.6667 | 2750 | 2750 | 2750 | 189.0625 | 184.8611 | 176.4583 | 157.1319 | 127.7222 | 84.0278 | 84.0278 | 84.0278 | #DIV/0! | 66.8624 | 81.6937 | 89.8102 | 92.3917 | 89.7733 | 89.7733 | 89.7733 | 81.8452 | 80.0265 | 76.3889 | 68.0225 | 55.291 | 36.3757 | 36.3757 | 36.3757
54 | 3240 | 90% | 81% | 72.9% | 54 | 450 | 900 | 1350 | 1800 | 2250 | 2700 | 2700 | 2700 | 182.25 | 178.2 | 170.1 | 151.47 | 123.12 | 81 | 81 | 81
53 | 3180 | 88.33% | 78.03% | 68.92% | 53 | 441.6667 | 883.3333 | 1325 | 1766.6667 | 2208.3333 | 2650 | 2650 | 2650 | 175.5625 | 171.6611 | 163.8583 | 145.9119 | 118.6022 | 78.0278 | 78.0278 | 78.0278
52 | 3120 | 86.67% | 75.11% | 65.1% | 52 | 433.3333 | 866.6667 | 1300 | 1733.3333 | 2166.6667 | 2600 | 2600 | 2600 | 169 | 165.2444 | 157.7333 | 140.4578 | 114.1689 | 75.1111 | 75.1111 | 75.1111
51 | 3060 | 85% | 72.25% | 61.41% | 51 | 425 | 850 | 1275 | 1700 | 2125 | 2550 | 2550 | 2550 | 162.5625 | 158.95 | 151.725 | 135.1075 | 109.82 | 72.25 | 72.25 | 72.25
50 | 3000 | 83.33% | 69.44% | 57.87% | 50 | 416.6667 | 833.3333 | 1250 | 1666.6667 | 2083.3333 | 2500 | 2500 | 2500 | 156.25 | 152.7778 | 145.8333 | 129.8611 | 105.5556 | 69.4444 | 69.4444 | 69.4444 | #DIV/0! | 50.2347 | 61.3777 | 67.4757 | 69.4152 | 67.448 | 67.448 | 67.448 | 67.6407 | 66.1376 | 63.1313 | 56.2169 | 45.695 | 30.0625 | 30.0625 | 30.0625
49 | 2940 | 81.67% | 66.69% | 54.47% | 49 | 408.3333 | 816.6667 | 1225 | 1633.3333 | 2041.6667 | 2450 | 2450 | 2450 | 150.0625 | 146.7278 | 140.0583 | 124.7186 | 101.3756 | 66.6944 | 66.6944 | 66.6944
48 | 2880 | 80% | 64% | 51.2% | 48 | 400 | 800 | 1200 | 1600 | 2000 | 2400 | 2400 | 2400 | 144 | 140.8 | 134.4 | 119.68 | 97.28 | 64 | 64 | 64
47 | 2820 | 78.33% | 61.36% | 48.07% | 47 | 391.6667 | 783.3333 | 1175 | 1566.6667 | 1958.3333 | 2350 | 2350 | 2350 | 138.0625 | 134.9944 | 128.8583 | 114.7453 | 93.2689 | 61.3611 | 61.3611 | 61.3611
46 | 2760 | 76.67% | 58.78% | 45.06% | 46 | 383.3333 | 766.6667 | 1150 | 1533.3333 | 1916.6667 | 2300 | 2300 | 2300 | 132.25 | 129.3111 | 123.4333 | 109.9144 | 89.3422 | 58.7778 | 58.7778 | 58.7778
45 | 2700 | 75% | 56.25% | 42.19% | 45 | 375 | 750 | 1125 | 1500 | 1875 | 2250 | 2250 | 2250 | 126.5625 | 123.75 | 118.125 | 105.1875 | 85.5 | 56.25 | 56.25 | 56.25 | #DIV/0! | 36.6211 | 44.7443 | 49.1898 | 50.6037 | 49.1696 | 49.1696 | 49.1696 | 54.789 | 53.5714 | 51.1364 | 45.5357 | 37.013 | 24.3506 | 24.3506 | 24.3506
44 | 2640 | 73.33% | 53.78% | 39.44% | 44 | 366.6667 | 733.3333 | 1100 | 1466.6667 | 1833.3333 | 2200 | 2200 | 2200 | 121 | 118.3111 | 112.9333 | 100.5644 | 81.7422 | 53.7778 | 53.7778 | 53.7778
43 | 2580 | 71.67% | 51.36% | 36.81% | 43 | 358.3333 | 716.6667 | 1075 | 1433.3333 | 1791.6667 | 2150 | 2150 | 2150 | 115.5625 | 112.9944 | 107.8583 | 96.0453 | 78.0689 | 51.3611 | 51.3611 | 51.3611
42 | 2520 | 70% | 49% | 34.3% | 42 | 350 | 700 | 1050 | 1400 | 1750 | 2100 | 2100 | 2100 | 110.25 | 107.8 | 102.9 | 91.63 | 74.48 | 49 | 49 | 49
41 | 2460 | 68.33% | 46.69% | 31.91% | 41 | 341.6667 | 683.3333 | 1025 | 1366.6667 | 1708.3333 | 2050 | 2050 | 2050 | 105.0625 | 102.7278 | 98.0583 | 87.3186 | 70.9756 | 46.6944 | 46.6944 | 46.6944
40 | 2400 | 66.67% | 44.44% | 29.63% | 40 | 333.3333 | 666.6667 | 1000 | 1333.3333 | 1666.6667 | 2000 | 2000 | 2000 | 100 | 97.7778 | 93.3333 | 83.1111 | 67.5556 | 44.4444 | 44.4444 | 44.4444 | #DIV/0! | 25.7202 | 31.4254 | 34.5476 | 35.5406 | 34.5334 | 34.5334 | 34.5334 | 43.29 | 42.328 | 40.404 | 35.9788 | 29.2448 | 19.24 | 19.24 | 19.24
39 | 2340 | 65% | 42.25% | 27.46% | 39 | 325 | 650 | 975 | 1300 | 1625 | 1950 | 1950 | 1950 | 95.0625 | 92.95 | 88.725 | 79.0075 | 64.22 | 42.25 | 42.25 | 42.25
38 | 2280 | 63.33% | 40.11% | 25.4% | 38 | 316.6667 | 633.3333 | 950 | 1266.6667 | 1583.3333 | 1900 | 1900 | 1900 | 90.25 | 88.2444 | 84.2333 | 75.0078 | 60.9689 | 40.1111 | 40.1111 | 40.1111
37 | 2220 | 61.67% | 38.03% | 23.45% | 37 | 308.3333 | 616.6667 | 925 | 1233.3333 | 1541.6667 | 1850 | 1850 | 1850 | 85.5625 | 83.6611 | 79.8583 | 71.1119 | 57.8022 | 38.0278 | 38.0278 | 38.0278
36 | 2160 | 60% | 36% | 21.6% | 36 | 300 | 600 | 900 | 1200 | 1500 | 1800 | 1800 | 1800 | 81 | 79.2 | 75.6 | 67.32 | 54.72 | 36 | 36 | 36
35 | 2100 | 58.33% | 34.03% | 19.85% | 35 | 291.6667 | 583.3333 | 875 | 1166.6667 | 1458.3333 | 1750 | 1750 | 1750 | 76.5625 | 74.8611 | 71.4583 | 63.6319 | 51.7222 | 34.0278 | 34.0278 | 34.0278 | #DIV/0! | 17.2305 | 21.0525 | 23.1442 | 23.8094 | 23.1347 | 23.1347 | 23.1347 | 33.1439 | 32.4074 | 30.9343 | 27.5463 | 22.3906 | 14.7306 | 14.7306 | 14.7306
34 | 2040 | 56.67% | 32.11% | 18.2% | 34 | 283.3333 | 566.6667 | 850 | 1133.3333 | 1416.6667 | 1700 | 1700 | 1700 | 72.25 | 70.6444 | 67.4333 | 60.0478 | 48.8089 | 32.1111 | 32.1111 | 32.1111
33 | 1980 | 55% | 30.25% | 16.64% | 33 | 275 | 550 | 825 | 1100 | 1375 | 1650 | 1650 | 1650 | 68.0625 | 66.55 | 63.525 | 56.5675 | 45.98 | 30.25 | 30.25 | 30.25
32 | 1920 | 53.33% | 28.44% | 15.17% | 32 | 266.6667 | 533.3333 | 800 | 1066.6667 | 1333.3333 | 1600 | 1600 | 1600 | 64 | 62.5778 | 59.7333 | 53.1911 | 43.2356 | 28.4444 | 28.4444 | 28.4444
31 | 1860 | 51.67% | 26.69% | 13.79% | 31 | 258.3333 | 516.6667 | 775 | 1033.3333 | 1291.6667 | 1550 | 1550 | 1550 | 60.0625 | 58.7278 | 56.0583 | 49.9186 | 40.5756 | 26.6944 | 26.6944 | 26.6944
30 | 1800 | 50% | 25% | 12.5% | 30 | 250 | 500 | 750 | 1000 | 1250 | 1500 | 1500 | 1500 | 56.25 | 55 | 52.5 | 46.75 | 38 | 25 | 25 | 25 | #DIV/0! | 10.8507 | 13.2576 | 14.5748 | 14.9937 | 14.5688 | 14.5688 | 14.5688 | 24.3506 | 23.8095 | 22.7273 | 20.2381 | 16.4502 | 10.8225 | 10.8225 | 10.8225
[7 empty] | 100 | 77 | 58
[14 empty] | 97.4026 | 95.2381 | 90.9091 | 80.9524 | 65.8009 | 43.29 | 43.29 | 43.29
[14 empty] | 81.8452 | 80.0265 | 76.3889 | 68.0225 | 55.291 | 36.3757 | 36.3757 | 36.3757
[6 empty] | (*See instructions below when entering fewer than eight points) H1: 67.6407; (*See instructions below when entering fewer than eight points) H2: 66.1376; (*See instructions below when entering fewer than eight points) H3: 63.1313; (*See instructions below when entering fewer than eight points) H4: 56.2169; (*See instructions below when entering fewer than eight points) H5: 45.695; (*See instructions below when entering fewer than eight points) H6: 30.0625; (*See instructions below when entering fewer than eight points) H7: 30.0625; (*See instructions below when entering fewer than eight points) H8: 30.0625 | system head in psi
[6 empty] | (*See instructions below when entering fewer than eight points) H1: 54.789; (*See instructions below when entering fewer than eight points) H2: 53.5714; (*See instructions below when entering fewer than eight points) H3: 51.1364; (*See instructions below when entering fewer than eight points) H4: 45.5357; (*See instructions below when entering fewer than eight points) H5: 37.013; (*See instructions below when entering fewer than eight points) H6: 24.3506; (*See instructions below when entering fewer than eight points) H7: 24.3506; (*See instructions below when entering fewer than eight points) H8: 24.3506 | sh1 | sh2 | sh3 | sh4 | sh5 | sh6 | sh7 | sh8
[6 empty] | (*See instructions below when entering fewer than eight points) H1: 43.29; (*See instructions below when entering fewer than eight points) H2: 42.328; (*See instructions below when entering fewer than eight points) H3: 40.404; (*See instructions below when entering fewer than eight points) H4: 35.9788; (*See instructions below when entering fewer than eight points) H5: 29.2448; (*See instructions below when entering fewer than eight points) H6: 19.24; (*See instructions below when entering fewer than eight points) H7: 19.24; (*See instructions below when entering fewer than eight points) H8: 19.24 | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126
[14 empty] | 33.1439 | 32.4074 | 30.9343 | 27.5463 | 22.3906 | 14.7306 | 14.7306 | 14.7306
[14 empty] | 24.3506 | 23.8095 | 22.7273 | 20.2381 | 16.4502 | 10.8225 | 10.8225 | 10.8225
[6 empty] | 3) To plot a system (constant pressure) curve, enter the | [7 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
[6 empty] | system heads (in ft) in SH1 - SH8 (Cells P62 - W62) that | [7 empty] | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
| INSTRUCTIONS: | [12 empty] | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126 | 54.1126
correspond to the flows in Q1 - Q8. (See Instructions below)
[6 empty] | 4) Enter the pump's hydraulic efficiencies in Ef 1 - Ef 8 | [7 empty] | Ef 1 | Ef 2 | Ef 3 | Ef 4 | Ef 5 | Ef 6 | Ef 7 | Ef 8
[6 empty] | (Cells P68 - W68) that correspond to the flows in Q1 - Q8 | [8 empty] | 0.64 | 0.75 | 0.81 | 0.8 | 0.65 | 0.65 | 0.65
Enter as a decimal equivalent. (See instructions below)
Click on the "Feet" or "PSI" tabs to view pump performance.
| AFFINITY LAW CALCULATOR | [5 empty] | CPSA Instructions
The Centrifugal Pump Selection Assistant (CPSA) allows you to compare the operating frequency range of a given pump
to the system conditions it must match in a level control or Constant Pressure / Variable Flow (CP/VF) application. You
can evaluate different pumps so that you can select the one that offers the best power savings and range of control. It
also allows you to demonstrate the advantages of VFD control over constant speed in many applications. For an overview
of constant pressure applications including level control, see the "VFD Pump Selection" tutorials on my web site.
Frequency and pump speed are synonymous, so the actual speed of the pump is not important. What is important is the
frequency (or speed) range. It is this range that dictates the potential power savings attainable by the application when
operating in a variable speed mode.
Step 1
Enter the pump description as you would like it to appear on the charts.
Step 2
| Enter a motor speed for 60 Hz | [5 empty] | Auto Plot requires that you enter eight, 60 Hz operating points in the row with the yellow background. Flows are entered
| operation in the cell with the | [5 empty] | beneath Q1 - Q8 and the corresponding heads are entered beneath H1 - H8. It is not necessary to begin with shutoff head
| yellow background and motor | [5 empty] | unless the pump will operate to the far left of the curve. Corresponding flows and heads are calculated for each point from
| speeds at the lower frequencies | [5 empty] | 59 - 30 Hz, however, Auto Plot displays the curves in 5hz increments (i.e. 55, 50, 45, etc). The labels displayed at each
| will be displayed. Note that the | [5 empty] | xy intercept on the head / capacity curves is the BHP required at that point. *If you wish to enter fewer than eight points,
enter the last point multiple times. For example if you have only six points, enter the data in Q6/H6 again in both Q7/H7
and Q8/H8. The same will hold true for Steps 3 & 4.
Step 3
In a constant pressure application, the system curve is the TDH required to maintain some predetermined pressure plus any
elevation and friction in the system. As flow and friction increase, the curve may slope upwards. *As in Step 2, enter the
last point multiple times if fewer than eight points are entered. Enter the system head for each flow point beneath SH1 - SH8.
Step 4
PPSA calculates BHP at each xy intercept on the head / capacity curves using the equation (q*h) / (3960*eff). Enter the
hydraulic efficiency of points Q1 - Q8 beneath Ef 1 - Ef 8. Enter as a decimal equivalent, not a whole number. If Q1 is zero,
leave Ef 1 blank (the data lable for blanks will indicate DIV/0). Follow the instructions above for fewer than eight points.
Click on the Feet and PSI Tabs to view the results.
The Example
The example included is a Berkeley B6EXPBL. The flow points entered are 500 - 3000 gpm. Note that the 3000 gpm flow and
head points are re-entered in Q7/H7 and Q8/H8. The same is true for the efficiency points Ef7 and Ef8. Also note that
is no efficiency value for Ef1 since one was not shown on the catalog curve.
The system curve shows a desired constant pressure of 125'. At this pressure, flow ranges from a minimum of approximately
500 gpm to 3750 gpm. Note that the Data Labels on each of the frequency curves show the BHP required at that flow / head
point. Based on the 60hz curve, if this pump were installed with PRV, it would consume approximately 119 BHP at 3750 gpm
and somewhat less than 87 hp at 750 gpm. This represents a power reduction of about 30% from maximum to minimum flow.
Now, take a look at the frequency curves the system curve crosses when the pump is under VFD control. Again, at maximum
flow the power required is approximately 119 BHP. But, since minimum flow can be supported at approximately 45hz, only
37 BHP is required. This represents a power reduction of approximately 69% from maximum to minium flow.
Note also that the hydraulic efficiency of any flow / head point moves to the left as frequency and therefore pump speed is
reduced. For example the 60hz efficiency of 81% at 2000 gpm remains the same at the 50hz flow of 1667 gpm. Ordinarily,
I would not support leftward migration but, in this case, it is good as it enhances power reduction.
http://www.pumped101.com