## Sheet1
PUMP CYCLE CALCULATOR
INPUT DATA
Wet Well Diameter (inches) |  | 96 | [5 empty] | 8 | convert inches to feet
Pump Down Distance (feet) |  | 3 | [5 empty] | 4 | calculate radius ft
Average Pump Flow (gpm) |  | 500 | [5 empty] | 50.24 | wet well surface area ft2
Surcharge Volume (if applicable) |  | 0
Average InFlow (gpm) |  | 50 | 100 | 150 | 200 | 250 | 300 | 150.72 | pump down volume ft3
CALCULATED RESULTS
Pump Down Volume (gal) |  | 1127.3856
Wet Well Fill Time (min) |  | 22.5477 | 11.2739 | 7.5159 | 5.6369 | 4.5095 | 3.758
Run Time (min) No inflow |  | 2.2548
Run Time (min) With Inflow |  | 2.5053 | 2.8185 | 3.2211 | 3.758 | 4.5095 | 5.6369 | 22.5477 | inflow fill time min
Starts / hr With Inflow |  | 2.3949 | 4.2576 | 5.5882 | 6.3865 | 6.6526 | 6.3865 | 25.053 | fill + run time min
Starts / Hour versus Inflow in GPM
Enter the required data in cells D8 through D12. You may enter
additional inflows in cells D12 through H12 for a comparison.
If a surcharge volume is entered in D11, it will be included in
in all calculations.
Starts / hour graph
Inflow | 50 | 55.5556 | 62.5 | 71.4286 | 83.3333 | 100 | 125 |  |  |  |  | 166.6667 | 250 | 333.3333 | 416.6667 | 454.5455
Run time | 2.5053 | 2.5366 | 2.5769 | 2.6306 | 2.7057 | 2.8185 | 3.0064 | 0 | #VALUE! | #DIV/0! | #DIV/0! | 3.3822 | 4.5095 | 6.7643 | 13.5286 | 24.8025
Starts / hour | 2.3949 | 2.6282 | 2.9105 | 3.2584 | 3.6959 | 4.2576 | 4.9894 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 5.9134 | 6.6526 | 5.9134 | 3.6959 | 2.1992