## Sheet1
SIMPLE WASTEWATER PUMP DRAW DOWN CALCULATOR
INPUT DATA
Wet Well Diameter (inches) | 144 | 12 | convert inches to feet
Pump Down Distance (inches) | 12 | 1 | convert inches to feet
Pump Down Time (seconds) | 30 | 0.5 | convert seconds to minutes
Discharge Gauge Pressure (PSI) | 22 | 50.82 | convert PSI to feet
Gauge Location to Water Level (inches) | 120 | 10 | convert inches to feet
Discharge Pipe ID @ Gauge (inches) | 6
Pump to Gauge Friction Loss (ft)** | 5
Inflow Distance (inches) | 0 | 0 | convert inches to feet
Inflow Time (seconds) | 0 | 0 | convert seconds to minutes
CALCULATED RESULTS
Wet Well Volume / Foot (Gal) | 845.5392
Draw Down Volume (Gal) | 845.5392
Flow Rate (GPM No Inflow) | 1691.0784
Discharge Velocity @ Gauge (ft/sec) | 19.189
Discharge Velocity Head (ft) | 5.7177
TDH Pump Discharge (ft) | 71.5377
TDH Pump Discharge (PSI) | 30.9687
Inflow Volume (Gal) | 0
Total Flow Rate (Gal) | 1691.0784 | #DIV/0!
Notes & Directions
Enter vertical distance from the Pump On Water Level to discharge gauge location in cell C9.
**Calculate the friction loss based upon the the discharge velocity (C19) and pipe length from pump to gauge. Use a friction table for the pipe size.
Use a calibrated gauge that reads the measured pressure near the mid point of the gauge range.
It is always best to perform a drawdown test with the invert off. If you cannot close it, perform the test during a time when inflow is lowest.
To account for inflow, perform an inflow test immediately after the drawdown test. To perform the inflow test, turn the pump off and
record the time required for the wet well level to rise 2 to 3 inches. Enter the time and level increase in cells C12 and C13. If inflow is not
a factor enter 0 in cells C12 and C13. It is always best to do at least two drawdown tests (and inflow tests if required) in order to get a more
accurate flow rate.