## Sheet1
System Energy Calculator
REQUIRED DATA | Option 1 |  |  | Option 2
System Condition: | Steel Pipe |  |  | Steel Pipe
| 8" 600' |  |  | 6" 600'
Pump Operation - Hours / Day | 8 |  |  | 8
Pump Operation - Days / Year | 365 |  |  | 365
Pump Flow - GPM | 600 |  |  | 600 | 12020 SE 32nd Street #2
Pump Head - Feet | 50 |  |  | 65 | Bellevue, WA 98005
Pump Efficiency - % | 71% |  |  | 71% | 888-644-6686
Motor Efficiency - % | 82% |  |  | 82%
Energy Cost in $/KWH | 0.11 |  |  | 0.11 | 2425 SE Ochoco Street
Portland, OR 97222
RESULTS |  |  |  |  | 503-659-6230
BHP At Design Point | 10.6701 |  |  | 13.8711
Wire to Water Efficiency - % | 58.22% |  |  | 58.22% | 209 S Hamilton Road
Annual Energy Cost | 3117.9434 | 9.7072 | 12.6193 | 4053.3265 | Moses Lake, WA 98837
KW Per 1000 Gallons Pumped | 0.26964 | 1.6667 | 1.6667 | 0.35054 | 509-766-6330
Cost Per 1000 Gallons Pumped | 0.029661 |  |  | 0.038559
PAYBACK
Annual Savings - $$ | 935.383 |  |  | Note: When comparing two options, place the lower
Annual Savings - % | 23.08% |  |  | efficiency option in the Option 2 column. If the pump
Cost of Option 1 | 12000 |  |  | or parallel pumps in Option 2 cannot meet the flow of
Cost of Option 2 | 9000 |  |  | of Option 1, increase the Hours / Day of operation to
Payback - Years | 3.2072 |  |  | make up the difference. Be sure to correct the overall
hydraulic efficiency when pumps are running in parallel.