## Above Ground Pumps
Centrifugal Pump Field Test Procedure (Suction & Discharge Gauge Measurement)
Manufacturer / Model # / etc | 3 X 4 X 11 - 1750 RPM - 10.75" Trim | [6 empty] | Entered Data |  | Calculated Results
Job Name | Yellow Water Supply | [5 empty] | Printing - | Set to landscape @ 75% of full size
Date | 2013-08-13 | Witness |  | Maxine Waters
Motor Serial Number | 6666 | Specific Gravity |  | 1 | Liquid Temp | 60⁰F | Calculations:
Pump Serial Number | 666666 | Q Measurement Method |  | Flowmeter |  |  | TDH = (Hd + GG + Fs + Fd + Hvd - Hs - Hvs)
Time of Day | 12:00 | [5 empty] | Hd = | discharge gauge pressure in feet
Ambient Temp | 70⁰F | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F | GG = | vertical distance between gauges in feet
Motor Temp | 265⁰F | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F | Fs = | friction - pump suction to suction gauge
Vibration (in/sec peak to peak) | [6 empty] | Fd = | friction - pump discharge to discharge gauge
[7 empty] | Hvd= | velocity head at the discharge gauge
Pump | Single or Multi Point Test |  |  | **See Instructions |  |  | Hs = | suction gauge pressure in feet
[7 empty] | Hvs= | velocity head at the suction gauge
Flow Rate (GPM) | 100 | 200 | 300 | 400 | 500 | 600
Suction Gauge Head ± (ft) | 2 | 2 | 2 | 2 | 2 | 2 | Velocity (V) = (Q * 0.4085) / ID2
Gauge to Suction Friction (ft) | 0 | 0 | 0 | 0 | 0 | 0 | Q = flow rate (gpm)
Suction Piping ID (in) | 5 | 5 | 5 | 5 | 5 | 5 | ID = pipe inner diameter
Discharge Gauge Head (ft) | 117 | 116 | 113 | 107 | 98 | 84 | 0.4085 = conversion constant
Gauge to Gauge Elevation (ft) | 2 | 2 | 2 | 2 | 2 | 2
Discharge to Gauge Friction (ft) | 0 | 0 | 0 | 0 | 0 | 0 | Velocity Head (Hv) = V2 / 2g
Discharge Piping ID (in) | 3 | 3 | 3 | 3 | 3 | 3 | V= flow velocity
Suction Velocity (fps) | 1.634 | 3.268 | 4.902 | 6.536 | 8.17 | 9.804 | g = gravitational constant (32 ft/sec2)
Suction Hv (ft) | 0.041459 | 0.16584 | 0.37313 | 0.66334 | 1.0365 | 1.4925
Discharge Velocity (fps) | 4.5389 | 9.0778 | 13.6167 | 18.1556 | 22.6944 | 27.2333 | BHP @ Test Point = (1.732 * Va * Aa * E * PF) / 746
Discharge Hv (ft) | 0.3199 | 1.2796 | 2.8791 | 5.1184 | 7.9975 | 11.5164 | BHP @ Test Point = (kW * E) / 0.746
TDH (ft) | 117.2784 | 117.1138 | 115.506 | 111.455 | 104.961 | 94.0239 | Va = | average voltage
[7 empty] | Aa = | average amperage
Motor - 3 Phase | [6 empty] | E = | motor efficiency
[7 empty] | PF = | power factor
Voltage - Phase a to b | 460 | 460 | 460 | 460 | 460 | 460 | 1.732 = | Υ/Δ constant
Voltage - Phase b to c | 460 | 460 | 460 | 460 | 460 | 460 | 746 = | watts / hp @ 100% eff
Voltage - Phase c to a | 460 | 460 | 460 | 460 | 460 | 460 | KW = | KW meter reading
Amperage - Phase a | 12 | 14 | 16.5 | 19 | 21.5 | 24
Amperage - Phase b | 12 | 14 | 16.5 | 19 | 21.5 | 24 | Hydraulic (Water) HP = (Q * H * SG) / 3960
Amperage - Phase c | 12 | 14 | 16.5 | 19 | 21.5 | 24 | Q = | flow rate (gpm)
Motor Efficiency (XX) | 91% | 91% | 91% | 91% | 91% | 91% | H = | TDH
Motor or Measured PF (XX) | 81% | 81% | 81% | 81% | 81% | 81% | SG = | specific gravity
kW Meter Reading (kW)** | 7.5 | 9 | 10.8 | 12.2 | 13.5 | 15.5 | 3960 = | conversion constant
Power Cost / kWhour (.00) | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
Average Voltage | 460 | 460 | 460 | 460 | 460 | 460 | Pump Efficiency = Hydraulic HP / BHP
Voltage Unbalance | 0% | 0% | 0% | 0% | 0% | 0%
Average Amperage | 12 | 14 | 16.5 | 19 | 21.5 | 24 | Cost / 1000 Gal Pumped = (.189*kWH Cost*Head)/
Current Unbalance | 0% | 0% | 0% | 0% | 0% | 0% |  |  | (Pump eff*Mtr eff*60)
Hydraulic (Water) HP @ 100% Eff | 2.9616 | 5.9148 | 8.7505 | 11.2581 | 13.2527 | 14.246
Motor BHP @ Test Point (VA) | 9.4466 | 11.021 | 12.989 | 14.9571 | 16.9251 | 18.8932
Motor BHP @ Test Point (kW) | 9.1488 | 10.9786 | 13.1743 | 14.882 | 16.4678 | 18.9075
Pump Eff @ Test Point (VA) | 31.35% | 53.67% | 67.37% | 75.27% | 78.3% | 75.4%
Pump Eff @ Test Point (kW) | 32.37% | 53.88% | 66.42% | 75.65% | 80.48% | 75.35%
voltage deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
current deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
Cost / 1000 Gal Pumped (VA) | 0.12949 | 0.075536 | 0.05935 | 0.051257 | 0.046401 | 0.043164
Cost / 1000 Gal Pumped (kW) | 0.12541 | 0.075245 | 0.060196 | 0.051 | 0.045147 | 0.043196 | Bellevue WA - Moses Lake WA - Canby OR
Additional Information
Notes
Signatures:
|  | Terry Aki |  |  |  |  | Doug Fir

## Submersible Wastewater (1)
Submersible Wastewater Pump Field Test Procedure (Discharge Gauge & Flow Meter Measurement)
Manufacturer / Model # / etc | Hydromatic S6L - 1750 RPM - 11.38" Trim |  |  |  | Printing - | Set to landscape @ 75% of full size
Job Name | Crap Creek Lift Station |  |  |  |  | Entered Data |  | Calculated Results
Date: | 2010-08-13 | Witness | Charles Rangel
Motor Serial Number | 123456 | Liquid SG & Temp | 1 | 60⁰F | Calculations:
Pump Serial Number | 654321 | Q Measurement | Flow Meter |  | TDH = Hd + GW + F + Hvd - Hvs
Time of Day | 9:00 |  |  |  | Where | Hd = | discharge gauge pressure (ft)
Ambient Temperature | 71⁰F | ⁰F | ⁰F | ⁰F |  | GW = | vertical distance between the
Vibration (in/sec peak to peak) | [6 empty] | gauge and wet well level
[6 empty] | F = | friction in the discharge piping
from pump to gauge
Pump | Single or Multi Point Test |  | **See Instructions |  |  | Hvd= | velocity head at the discharge gauge
[6 empty] | Hvs= | velocity head at the pump suction
Flow Meter (GPM) | 400 | 800 | 1200 | 1600
Discharge Gauge to Waterline (ft) | 10 | 10 | 10 | 10 | Velocity (V) = (Q * 0.4085) / ID2
Discharge Gauge Head (ft) | 99 | 86 | 71 | 51 | Where | Q = | flow rate (gpm)
Pipe Friction Pump to Gauge (ft) | 0.3 | 1.3 | 2.7 | 5 |  | ID = pipe inner diameter
Pump Suction Diameter (in)** | 12 | 12 | 12 | 12
Discharge Pipe ID (in) | 6 | 6 | 6 | 6 |  | 0.4085 = conversion constant
Discharge Velocity (fps) | 4.5389 | 9.0778 | 13.6167 | 18.1556
Discharge Velocity Head | 0.3199 | 1.2796 | 2.8791 | 5.1184 | Velocity Head (Hv) = V2 / 2g
Suction Velocity (fps) | 1.1347 | 2.2694 | 3.4042 | 4.5389 | Where | V= | flow velocity
Suction Velocity Head | 0.019994 | 0.079975 | 0.17994 | 0.3199 |  | g = | gravitational constant
TDH (ft) | 109.5999 | 98.4996 | 86.3992 | 70.7985
Motor - 3 Phase |  |  |  |  | BHP @ Test Point = (1.732 * Va * Aa * E * PF) / 746
BHP @ Test Point = (kW * E) / 0.746
Voltage - Phase a to b | 460 | 460 | 460 | 460 | Where | Va = | average voltage
Voltage - Phase b to c | 460 | 460 | 460 | 460 |  | Aa = | average amperage
Voltage - Phase c to a | 460 | 460 | 460 | 460 |  | E = | motor efficiency
Amperage - Phase a | 38 | 42 | 48 | 51 |  | PF = | power factor
Amperage - Phase b | 38 | 42 | 48 | 51 |  | 1.732 | Υ/Δ constant
Amperage - Phase c | 38 | 42 | 48 | 51 |  | 746 = | watts / hp
Motor Efficiency (XX) | 81% | 83% | 84% | 84% |  | KW = | KW meter reading
Motor or Measured PF (XX) | 84% | 86% | 86% | 86%
kW Meter Reading (kW)** | 25.2 | 28.5 | 32.7 | 35 | Hydraulic (Water) HP = (Q * H * SG) / 3960
Power Cost / kWhour (.00) | 0.11 | 0.11 | 0.11 | 0.11 | Where | Q = | flow rate (gpm)
Average Voltage | 460 | 460 | 460 | 460 |  | H = | TDH
Voltage Unbalance | 0% | 0% | 0% | 0% |  | SG = | specific gravity
Average Amperage | 38 | 42 | 48 | 51 |  | 3960 = | conversion constant
Current Unbalance | 0% | 0% | 0% | 0%
Hydraulic HP @ 100% Eff | 11.0707 | 19.8989 | 26.1816 | 28.6055 | Pump Efficiency = Hydraulic HP / BHP
Motor BHP @ Test Point (VA) | 27.6131 | 32.0179 | 37.0327 | 39.3473
Motor BHP @ Test Point (kW) | 27.3619 | 31.7091 | 36.8204 | 39.4102 | Cost / 1000 Gal Pumped = (.189*kWH Cost*Head)/(Pump eff*Mtr eff*60)
Pump Eff @ Test Point (VA) | 40.09% | 62.15% | 70.7% | 72.7%
Pump Eff @ Test Point (kW) | 40.46% | 62.75% | 71.11% | 72.58%
voltage deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
current deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
Cost / 1000 Gal Pumped (VA) | 0.11694 | 0.066164 | 0.050411 | 0.040171
Cost / 1000 Gal Pumped (kW) | 0.11588 | 0.065526 | 0.050122 | 0.040235 | Bellevue WA - Moses Lake WA - Canby OR
Additional Information
Notes
Signatures:
|  | Terry Aki |  |  | Doug Fir

## Submersible Wastewater (2)
Submersible Wastewater Pump Field Test Procedure (Discharge Gauge & Draw Down Measurement)
Manufacturer / Model # / etc | Hydromatic S6L - 1750 RPM - 11.38" Trim |  |  |  |  | Printing - | Set to landscape @ 75% of full size
Job Name | Crap Creek Lift Station | [5 empty] | Entered Data |  | Calculated Results
Date: | 2013-08-13 | Witness | Harry Reed
Motor Serial Number | 123456 | Liquid SG & Temp | 1 | 60⁰F |  | Calculations:
Pump Serial Number | 654321 | Q Measurement | Drawdown (1') |  |  | TDH = Hd + GW + F + Hvd - Hvs
Time of Day | 9:00 |  |  |  |  | Where | Hd = | discharge gauge pressure (ft)
Ambient Temperature | 71⁰F | [5 empty] | GW = | vertical distance between the
Vibration (in/sec peak to peak) | [7 empty] | gauge and wet well level
[7 empty] | F = | friction in the discharge piping
| **See Instructions |  |  |  | conversions |  |  | from pump to gauge
[5 empty] | inches to feet |  | Hvd= | velocity head at the discharge gauge
Pump Head Test |  |  | Drawdown Flow Test** |  | inches to feet |  | Hvs= | velocity head at the pump suction
seconds to minutes
Discharge Gauge to Waterline (ft) | 10 |  | Wet Well Diameter (Inches) | 144 | 12 | Velocity (V) = (Q * 0.4085) / ID2
Discharge Gauge Head (ft) | 51 |  | Drawdown Distance (Inches) | 12 | 1 | Where | Q = | flow rate (gpm)
Pipe Friction Pump to Gauge (ft) | 5 |  | Drawdown Time (Seconds) | 32 | 0.53333 |  | ID = pipe inner diameter
Pump Suction Diameter (in)** | 18 |  | Wet Well Volume / ft (Gal) | 845.5392 | conversions
Discharge Pipe ID (in) | 6 |  | Drawdown Volume (Gal) | 845.5392 | inches to feet |  | 0.4085 = conversion constant
Discharge Velocity (fps) | 17.9897 |  | Flow Rate (GPM No Inflow) | 1585.386 | seconds to minutes
Discharge Velocity Head | 5.0253 |  | Inflow Distance (Inches) | 0 | 0 | Velocity Head (Hv) = V2 / 2g
Suction Velocity (fps) | 1.9989 |  | Inflow Time (Seconds) | 0 | 0 | Where | V= | flow velocity
Suction Velocity Head | 0.062041 |  | Inflow Volume (Gal) | 0 | drawdown+inflow |  | g = | gravitational constant
TDH (ft) | 70.9633 |  | Total Flow Rate (GPM) | 1585.386 | #DIV/0!
Motor - 3 Phase | Running | Off |  |  |  | BHP @ Test Point = (1.732 * Va * Aa * E * PF) / 746
BHP @ Test Point = (kW * E) / 0.746
Voltage - Phase a to b | 460 | 460 |  |  |  | Where | Va = | average voltage
Voltage - Phase b to c | 460 | 460 |  |  |  |  | Aa = | average amperage
Voltage - Phase c to a | 460 | 460 |  |  |  |  | E = | motor efficiency
Amperage - Phase a | 52.5 | [5 empty] | PF = | power factor
Amperage - Phase b | 52.5 | [5 empty] | 1.732 | Υ/Δ constant
Amperage - Phase c | 52.5 | [5 empty] | 746 = | watts / hp
Motor Efficiency (XX) | 87% | [5 empty] | KW = | KW meter reading
Motor or Measured PF (XX) | 81%
kW Meter Reading (kW)** | 34.2 |  |  |  |  | Hydraulic (Water) HP = (Q * H * SG) / 3960
Power Cost / kWhour (.00) | 0.11 |  |  |  |  | Where | Q = | flow rate (gpm)
Average Voltage | 460 | 460 |  |  |  |  | H = | TDH
Voltage Unbalance | 0% | 0% |  |  |  |  | SG = | specific gravity
Average Amperage | 52.5 | [5 empty] | 3960 = | conversion constant
Current Unbalance | 0%
Hydraulic HP @ 100% Eff | 28.4101 |  |  |  |  | Pump Efficiency = Hydraulic HP / BHP
Motor BHP @ Test Point (VA) | 39.5121
Motor BHP @ Test Point (kW) | 39.8847 |  |  |  |  | Cost / 1000 Gal Pumped = (.189*kWH Cost*Head)/(Pump eff*Mtr eff*60)
Pump Eff @ Test Point (VA) | 71.9%
Pump Eff @ Test Point (kW) | 71.23%
voltage deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
current deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0
Cost / 1000 Gal Pumped (VA) | 0.039307
Cost / 1000 Gal Pumped (kW) | 0.039678 |  |  |  |  | Bellevue WA - Moses Lake WA - Canby OR
Additional Information
Notes
Signatures:
|  | Terry Aki |  |  |  | Doug Fir

## Vertical Turbine
Vertical Turbine Pump Field Test Procedure (Discharge Gauge & Flow Meter Measurement)
Manufacturer / Model # / etc | M-14-MC 1770 RPM 11.56" Trim | [5 empty] | Printing - | Set to landscape @ 75% of full size
Job Name | Over The Hill Pump Station | [6 empty] | Entered Data |  | Calculated Results
Date | 2013-08-13 | Witness |  | Rod Blagojevich
Motor Serial Number | 6666 | Specific Gravity |  | 1 | Liquid Temp | ⁰F
Pump Serial Number | 666666 | Q Measurement Method |  | Flowmeter |  |  | Calculations:
Time of Day | 12:00 | [5 empty] | TDH = Hd + GW + F + Hv
Ambient Temperature | 70⁰F | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F | Where | Hd = | discharge gauge pressure in feet
Motor Temperature | 265⁰F | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F |  | GW = | vertical distance between the
Stuffing Box Temperature | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F |  |  | gauge and water level in feet
Lwr Motor Bearing Temperature | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F | ⁰F |  | F = | friction in column and elbow in feet
Vibration (in/sec peak to peak) | [7 empty] | Hv= | velocity head at the gauge
Pump | **See Instructions | [5 empty] | Velocity (V) = (Q * 0.4085) / ID2
[7 empty] | Where | Q = | flow rate
Flow Rate (GPM) | 500 | 750 | 1000 | 1250 | 1500 | 1750 |  | ID = pipe inner diameter
Discharge Gauge to Waterline (ft) | 25 | 25 | 25 | 25 | 25 | 25 |  | 0.4085 conversion constant
Discharge Gauge Head (ft) | 348 | 343 | 335 | 317 | 288 | 251
Friction Loss (Column & Elbow ft) | 0.6 | 0.7 | 0.9 | 1 | 1.2 | 1.3 | Velocity Head (Hv) = V2 / 2g
Discharge Elbow (Pipe) ID | 12 | 12 | 12 | 12 | 12 | 12 | Where | V= | flow velocity
Discharge Velocity (fps) | 1.4184 | 2.1276 | 2.8368 | 3.546 | 4.2552 | 4.9644 |  | g = | gravitational constant
Velocity Head (Hv in ft) | 0.03124 | 0.07029 | 0.12496 | 0.19525 | 0.28116 | 0.38269
TDH (ft) | 373.6312 | 368.7703 | 361.025 | 343.1953 | 314.4812 | 277.6827
Motor - 3 Phase
Voltage - Phase a to b | 460 | 460 | 460 | 460 | 460 | 460 | BHP @ Test Point = (1.732 * Va * Aa * E * PF) / 746
Voltage - Phase b to c | 460 | 460 | 460 | 460 | 460 | 460 | BHP @ Test Point = (kW * E) / 0.746
Voltage - Phase c to a | 460 | 460 | 460 | 460 | 460 | 460 | Where | Va = | average voltage
Amperage - Phase a to b | 120 | 140 | 160 | 175 | 185 | 200 |  | Aa = | average amperage
Amperage - Phase b to c | 120 | 140 | 160 | 175 | 185 | 200 |  | E = | motor efficiency
Amperage - Phase c to a | 120 | 140 | 160 | 175 | 185 | 200 |  | PF = | power factor
Motor Efficiency (XX) | 91% | 91% | 91% | 91% | 91% | 91% |  | 1.732 | wye /delta constant
Motor or Measured PF (XX) | 81% | 81% | 81% | 81% | 81% | 81% |  | 746 | watts / hp
kW Meter Reading (kW)** | 77 | 90 | 104 | 113 | 119 | 129 |  | kW = kW meter reading
Shaft Losses /100 ft (HP) | 3 | 3 | 3 | 3 | 3 | 3
Shaft Length (ft) | 25 | 25 | 25 | 25 | 25 | 25 | Hydraulic HP = (Q * H * SG) / 3960
Power Cost / kWhour (.00) | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | Where | Q = | flow rate (gpm)
Average Voltage | 460 | 460 | 460 | 460 | 460 | 460 |  | H = | TDH
Voltage Unbalance | 0% | 0% | 0% | 0% | 0% | 0% |  | SG = specific gravity
Average Amperage | 120 | 140 | 160 | 175 | 185 | 200 |  | 3960 | conversion constant
Current Unbalance | 0% | 0% | 0% | 0% | 0% | 0%
Hydraulic HP @ 100% Eff | 47.1757 | 69.8429 | 91.1679 | 108.3318 | 119.1217 | 122.7133 | Pump Eff = Hydraulic HP / BHP (less shaft losses)
Motor HP @ Test Point (VA) | 94.4658 | 110.2101 | 125.9544 | 137.7626 | 145.6348 | 157.443
Motor HP @ Test Point (kW) | 93.9276 | 109.7855 | 126.8633 | 137.8418 | 145.1609 | 157.3592 | Cost / 1000 Gal Pumped = (.189*kWH Cost*Head)/(Pump eff*Mtr eff*60)
Total Shaft HP Loss | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
Test Point HP Less Shaft Loss (VA) | 93.7158 | 109.4601 | 125.2044 | 137.0126 | 144.8848 | 156.693
Test Point HP Less Shaft Loss (kW) | 93.1776 | 109.0355 | 126.1133 | 137.0918 | 144.4109 | 156.6092
Pump Eff @ Test Point (VA) | 50.34% | 63.81% | 72.82% | 79.07% | 82.22% | 78.31%
Pump Eff @ Test Point (kW) | 50.63% | 64.06% | 72.29% | 79.02% | 82.49% | 78.36%
Cost / 1000 Gal Pumped (VA) | 0.28262 | 0.22007 | 0.18879 | 0.16528 | 0.14564 | 0.13501
Cost / 1000 Gal Pumped (kW) | 0.281 | 0.21921 | 0.19016 | 0.16537 | 0.14517 | 0.13494 | Bellevue WA - Moses Lake WA - Canby OR
voltage deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
current deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
make all positive | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
select largest deviation | 0 | 0 | 0 | 0 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0
Additional Information
Notes
Signatures:
|  | Terry Aki |  |  |  |  | Doug Fir

## Instructions
Field Test Instructions
These field test templates are designed for universal usage and may require changes to meet certain test specifications.
They are divided into three separate installation categories - above ground pumps, submersible sewage and vertical turbines.
The above ground pumps include end suction, double suction, wastewater and self primers. The spread sheets provide for
multiple tests at the same operating point or single tests at multiple operating points. In the latter case, a test curve is generated
on page 3 if the test points for increasing flow are entered from left to right. A flowmeter is used to measure flow. The Vertical Turbine
tab can also be used for submersible well pumps and will also generate a test curve.
The Submersible wastewater (1) tab can be used for one or multiple test points and a flow meter is used to determine flow.
This tab will also plot a test curve if multiple points are tested. Scroll to the bottom of the sheet to view the test curves.
The Submersible Wastewater (2) tab is designed for a single point test to measure flow using drawdown. See below for
detailed instructions for measuring drawdown. Page 2 is reserved for notes, observations or test data not shown on page 1.
The data necessary to perform the calculations are self explanatory and the required units are shown to the left of the
cells. The equations used to calculate the results are shown on the right side of the spread sheet. The test point
HP is calculated using average amperage and voltage and / or measured kW. You can also use either or both. **Note that the
HP calculation that uses the kW assumes that power factor has been accounted for in the kW measurement. When a VFD is
used, a standard volt / amp meter can be used to measure voltage and current on the power imput side of the VFD.
**You will note that the TDH calculation for the Submersible Wastewater tabs include suction velocity head. There is disagreement in the
industry as to whether velocity head is a factor when testing a submersible pump with a suction bell. Personally, I do not think that it plays a role.
If you enter the actual suction diameter into the sheet, velocity head will be calculated based upon the calculated inlet velocity. If you do not
want it to be a factor, simply enter a suction diameter that lowers the velocity head calculation to nearly zero.
It is assumed that the suction and discharge gauges will be located at the centerlines. If they are substantially above
or below, correct the actual gauge readings before entering the test data. It is also assumed that the suction gauge
will be located close to the pump suction. If it is some distance from the suction, the friction in the piping between
gauge and the suction should be entered in the Fs cells.
Motor Testing
Measure the phase to phase voltage with the pump off. This allows you to determine if any unbalanced voltage is due to conditions
in your facility or is a result of the incoming utility power. Use the "motor off" section of the Submersible Wastewater (2) tab to calculate
average voltage and % voltage unbalance. Measure phase to phase voltage and current at each test point and enter them into the appropriate
cells. Take the measurements on the motor side of the contactor. Unbalanced voltage due to a corroded contactor will not be detected
if measured on the power side. The reason that both voltage and current unbalance are calculated is because some clamp on amp meters
are not as accurate as a volt meter. % current unbalance can be 6 to 10 times greater than voltage unbalance. If voltage unbalance is 2% or
more, the source must be located and corrected. An exception to this rule will apply if the phase with the highest current remains under
the nameplate amperage. If the motor power factor has been corrected by a capacitor bank, measure the PF with a PF meter.
Submersible Wastewater (2)
Drawdown Test: Turn the pumps off. Shut off the invert valve or insert a pig when the wet well is at the pump on level. Inflow during the
drawdown will make the results inaccurate. The ideal drawdown distance is one foot. A change in just one foot will keep flow very close to its
pump start value. Drawdown distance can be measured with a laser, plumb bob or a measuring tape. It is best to do two or three tests and use
the average drawdown time for the spreadsheet calculations. Measure the drawdown time in seconds.
Inflow Test: If the invert cannot be shut off, an inflow test is required if we are to get an accurate pump flow calculation. At the end of the
drawdown test, record the time for the wetwell leve to rise some predetermined distance. If the drawdown distance was one foot,
four to six inches is enough distance to measure inflow. Again several tests may be required to get a more accurate, average inflow measurement.
If possible, perform the drawdown and inflow tests during periods of minimum inflow.
Pump TDH Test: Make an accurate measurement of the elevation of the gauge above the pump start water level. Calculate the friction
in the length of pipe from the pump discharge to the point where the gauge is mounted. Use the flow rate calculated by the drawdown test.
If you do not want suction velocity head to be a factor in the TDH calculation, enter a suction diameter that will reduce the suction velocity
head calculation to near zero.
Motor Test: Measure the phase to phase voltage with the pump off. If a voltage unbalance exists with the pump off, it is caused by your
facility or the utility. Measure phase to phase voltage and current during the one foot draw down test (full flow). Take the measurements
on the pump side of the contactor. Unbalanced voltage due to a corroded contactor will not be detected if measured on the power side.
The reason that both voltage and current unbalance are calculated is because some clamp on, amp meters are not as accurate as a volt meter.
% current unbalance can be 6 to 10 times greater than voltage unbalance. If voltage unbalance is 2% or more, the source must be located and
corrected. An exception to this rule will apply if the phase with the highest current is still under the nameplate amperage.