## Sheet1
Off BEP Energy Cost Calculator
REQUIRED DATA | BEP |  |  | Off BEP
Pump Operation - Hours / Day | 8 |  |  | 8
Pump Operation - Days / Year | 365 |  |  | 365
Pump Flow - GPM | 5000 |  |  | 4000 | 12020 SE 32nd Street #2
Pump Head - Feet | 130 |  |  | 147 | Bellevue, WA 98005
Pump Efficiency - % | 87% |  |  | 83% | 888-644-6686
Motor Efficiency - % | 95% |  |  | 95%
Energy Cost in $/kWh | 0.1 |  |  | 0.1 | 321 S Sequoia Parkway
Canby, OR 97013
RESULTS |  |  |  |  | 503-659-6230
BHP At Operating Point | 188.6683 |  |  | 178.8974
Wire to Water Efficiency (%) | 82.65% |  |  | 78.85% | 209 S Hamilton Road
Annual Pumpage (gal) | 876000000 |  |  | 700800000 | Moses Lake, WA 98837
Annual Energy Consumption (kWh) | 432610.4359 |  |  | 410206.1067 | 509-766-6330
Annual Energy Cost | 43261.0436 | 148.1543 | 140.4815 | 41020.6107
kW Per 1000 Gallons Pumped | 0.49385 | 0.2 | 0.25 | 0.58534
Cost Per 1000 Gallons Pumped | 0.049385 |  |  | 0.058534