## PPPA
50Hz Parallel Pump Performance Analyzer with Variable Speed Options
Follow the five steps below to view the operation of multiple pumps operating in parallel.
Scroll down to row 60 for more detailed instructions.
[6 empty] | 1) Enter the chart title in yellow box # 1 |  |  |  | 1 | Cornell 5RB 1483 RPM 13.5" Trim
[6 empty] | Enter the flow units in yellow box # 2 |  |  |  | 2 | Flow = GPM
[6 empty] | Enter the head units in yellow box # 3 |  |  |  | 3 | Head = Feet
[6 empty] | Enter the piping data in box #4 |  |  |  | 4 | Piping = 1000', 12" Sch 40 Steel
These items will be displayed on the charts.
[6 empty] | 2) Enter the number of pumps in the yellow cell on the right |  |  |  |  | 3
| ENTER RPM IN CELL B22 |  |  |  |  | 3) Enter eight 60 hertz flows In Q1 - Q8 (Cells H20 - O20)
Enter the corresponding heads in H1 - H8 (Cells H22 - O22)
(See instructions below when entering fewer than eight points)
[6 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8
[6 empty] | 417 | 625 | 833 | 1042 | 1250 | 1458 | 1667 | 1875
[6 empty] | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
[6 empty] | 139 | 135 | 130 | 124 | 115 | 103 | 87 | 69
4) Enter the pump's hydraulic efficiency in Ef1 - Ef8 (Cells H27 - O27) that correspond to the flows in Q1 - Q8.
[6 empty] | Ef1 | Ef2 | Ef3 | Ef4 | Ef5 | Ef6 | Ef7 | Ef8
[6 empty] | 0.6 | 0.72 | 0.8 | 0.84 | 0.86 | 0.86 | 0.83 | 0.74
[6 empty] | 60% | 72% | 80% | 84% | 86% | 86% | 83% | 74%
5) To plot a system curve, enter the various flow points from minimum to maximum design flow in
SQ1 - SQ8 (Cells H36 - O36). Calculate the corresponding system heads and enter them in
SH1 - SH8 (Cells H38 - O38). Each value should contain elevation, pipe friction and valve / fitting
losses. (See instructions below)
[6 empty] | SQ1 | SQ2 | SQ3 | SQ4 | SQ5 | SQ6 | SQ7 | SQ8
[6 empty] | 0 | 750 | 1500 | 2250 | 3000 | 3750 | 4500 | 5250
[6 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
50 |  | 1 | 1 | 1 |  | 70 | 71 | 76 | 82 | 91 | 102 | 117 | 138
[5 empty] | 50 one | 417 | 625 | 833 | 1042 | 1250 | 1458 | 1667 | 1875 | 139 | 135 | 130 | 124 | 115 | 103 | 87 | 69
[5 empty] | 45 one | 375.3 | 562.5 | 749.7 | 937.8 | 1125 | 1312.2 | 1500.3 | 1687.5
[5 empty] | 40 one | 333.6 | 500 | 666.4 | 833.6 | 1000 | 1166.4 | 1333.6 | 1500
[5 empty] | 35 one | 291.9 | 437.5 | 583.1 | 729.4 | 875 | 1020.6 | 1166.9 | 1312.5
[5 empty] | 30 one | 250.2 | 375 | 499.8 | 625.2 | 750 | 874.8 | 1000.2 | 1125
[5 empty] | 50 mult | 1251 | 1875 | 2499 | 3126 | 3750 | 4374 | 5001 | 5625
45 |  | 0.9 | 0.81 | 0.729 | 45 mult | 1125.9 | 1687.5 | 2249.1 | 2813.4 | 3375 | 3936.6 | 4500.9 | 5062.5 | 112.59 | 109.35 | 105.3 | 100.44 | 93.15 | 83.43 | 70.47 | 55.89
40 |  | 0.8 | 0.64 | 0.512 | 40 mult | 1000.8 | 1500 | 1999.2 | 2500.8 | 3000 | 3499.2 | 4000.8 | 4500 | 88.96 | 86.4 | 83.2 | 79.36 | 73.6 | 65.92 | 55.68 | 44.16
35 |  | 0.7 | 0.49 | 0.343 | 35 mult | 875.7 | 1312.5 | 1749.3 | 2188.2 | 2625 | 3061.8 | 3500.7 | 3937.5 | 68.11 | 66.15 | 63.7 | 60.76 | 56.35 | 50.47 | 42.63 | 33.81
30 |  | 0.6 | 0.36 | 0.216 | 30 mult | 750.6 | 1125 | 1499.4 | 1875.6 | 2250 | 2624.4 | 3000.6 | 3375 | 50.04 | 48.6 | 46.8 | 44.64 | 41.4 | 37.08 | 31.32 | 24.84
[5 empty] | 2 | 834 | 1250 | 1666 | 2084 | 2500 | 2916 | 3334 | 3750
[5 empty] | 3 | 1251 | 1875 | 2499 | 3126 | 3750 | 4374 | 5001 | 5625
[5 empty] | 4 | 1668 | 2500 | 3332 | 4168 | 5000 | 5832 | 6668 | 7500
[5 empty] | 5 | 2085 | 3125 | 4165 | 5210 | 6250 | 7290 | 8335 | 9375
[5 empty] | 6 | 2502 | 3750 | 4998 | 6252 | 7500 | 8748 | 10002 | 11250
[5 empty] | 7 | 2919 | 4375 | 5831 | 7294 | 8750 | 10206 | 11669 | 13125
[5 empty] | 8 | 3336 | 5000 | 6664 | 8336 | 10000 | 11664 | 13336 | 15000
Click on the "One Pump" tab to view single pump performance. Click on the "Composite Curves" tab to view
multiple pump performance. You can also enter different values in the "Number of Pumps Cell" and review
the "Composite Curves" for a fewer or greater number of pumps. You will also see how variable speed will effect
single and multiple pump performance. The "Traditional" tabs show traditional views of the various combinations.
Joe Evans, Ph.D Updated 7/23/2013
AFFINITY LAW CALCULATOR
Instructions
The Parallel Pump Performance Analyzer will allow you to view the performance of multiple pumps operating in parallel.
I supports any number of pumps and also shows the effect of speed change on various combinations.
Step 1
Enter the information that you would like displayed on the charts. Flow and head can be any units.
Enter a motor speed for 60 Hz
| operation in the cell with the |  |  |  |  | SH1: Step 2
yellow background and motor
| speeds at the lower frequencies |  |  |  |  | SH1: Enter the maximum number of pumps that will be operated in parallel. The analyzer assumes that each of the pumps will
have the same performance characteristics.
Step 3
Enter up to eight flow and head points based upon the pump 50 HZ performance curve. The frist entry does not have to be zero and can be
a higher value. If you enter fewer that eight points, enter the last one multiple times. For example if you enter only six points, place
the last one in Q7/H7 and Q8/H8 also.
Step 4
Enter the hydraulic efficiency for each of the H/Q points. Enter as a decimal equivalent.
Step 5
A system curve is absolutely essential when evaluating pumps operating in parallel. Enter up to eight system flow points based
upon the minimum and maximum design flows. Calculate the system head for each point and enter them is the cell below each
of the flow points. The total system head for each point should include elevation or static pressure, pipe friction and any valve
and fitting losses.
The Example
The example requires a multipump system that will supply a maximum flow of 5000 GPM at a head of 155'. The total head consists of
110' of elevation and the friction that arises in 1000' of 12" diameter schedule 40 steel pipe. The minimum flow rate required is 1500 GPM.
Several intermediate flows are also required. The "Traditional 3" tab shows three 5RB pumps running in parallel at 60hz. These meet
the maximum flow requirement at 86% hydraulic efficiency. The "One Pump" tab shows that a single pump cannot meet the minimum
flow rate at full speed. It can, however, meet it at 52hz. The "Composite Curves" tabs shows three pumps in parallel under variable speed control.
It shows that they can maintain 86% eff down to 4000gpm. If you change the number of pumps to two, the "Composite Curves" tab shows that
[6 empty] | two pumps can deliver 2500 - 3200gpm at 86% eff. |  |  |  | If 2000gpm is needed, you will have to live with 84% eff. Not bad actually.
http://www.pumped101.com