## Data Input
Simplex / Duplex System Curve Analyzer
Joe Evans, Ph.D 12/14/07
Follow the steps below to compare the performance of single and duplex pumps to a system curve.
Use the "Notes" tab to maintain your detailed system data and calculations.
Scroll down to row 46 for more detailed instructions and comments on the included example.
1) Enter simplex design flow in cell D20
2) Enter the elevation from the minimum pump down level* to the pipe discharge in cell H20
3) Enter the force main pressure (if applicable) in feet in cell D22
4) Enter the "equivalent" pipe length for the discharge pipe and fittings in cell H22
5) Enter the friction loss per 100' of pipe in cells D25 - L25
6) Enter up to nine* single pump flows (Q) in cells D28 - L28
7) Enter corresponding heads (H) in cells D29 - L29
8) Enter pump description in cell D31
9) Enter the pipe description in cell K31
10) Click on the "Analyzer" tab to review the results
DESIGN FLOW | 600 |  | ELEVATION |  | 47
FM PRESSURE | 0 |  | EQ PIPE LENGTH |  | 381
FLOW | 0 | 150 | 300 | 450 | 600 | 750 | 900 | 1050 | 1200
FRICTION (per100') | 0 | 0.36 | 1.32 | 2.74 | 4.65 | 7.12 | 10.11 | 13.2 | 17.1
FLOW / HEAD | Q1 / H1 | Q2 / H2 | Q3 / H3 | Q4 / H4 | Q5 / H5 | Q6 / H6 | Q7 / H7 | Q8 / H8 | Q9 / H9
FLOW (Q) | 0 | 100 | 200 | 300 | 400 | 500 | 600 | 700 | 800
HEAD (H) | 121 | 105 | 95 | 87 | 79 | 72 | 65 | 57 | 49
PUMP DESC | Q1 / H1: H4HX 1750 RPM, Trim 10", 71% eff; Q6 / H6: PIPE DESC; Q8 / H8: 300' 6" Steel Pipe
Equiv Friction | 0 | 1.3716 | 5.0292 | 10.4394 | 17.7165 | 27.1272 | 38.5191 | 50.292 | 65.151
Sys Flow Parallel | 0 | 150 | 300 | 450 | 600 | 750 | 900 | 1050 | 1200
Sys Head Parallel | 47 | 48.3716 | 52.0292 | 57.4394 | 64.7165 | 74.1272 | 85.5191 | 97.292 | 112.151
Parallel Pumps
Parallel Head | 121 | 105 | 95 | 87 | 79 | 72 | 65 | 57 | 49
Parallel Flow | 0 | 200 | 400 | 600 | 800 | 1000 | 1200 | 1400 | 1600
Simplex / Duplex Sytem Curve Analyzer Instructions
The SDSC Analyzer allows you to generate a system curve and then evaluate the same pump under simplex and
duplex operation. It will allow you to see how a single pump will react to dynamic changes in head and also
how much the second pump will contribute to overall flow. All data is entered into the yellow blocks in the
Data Input tab. The Notes tab allows you to retain all pertinent information and manual calculations. The
information used in the included example can be found under this tab.
Step 1
Calculate and enter the design flow for simplex operation in the yellow block at cell D20. This will cause a marker
to be placed on the system curve at the design point. It will also populate line 24 with a group of flow rates.
Step 2
Enter the elevation from the lowest level in the wet well to the exit of the discharge pipe in cell H20. This will be used as the
static head component of the system curve. Some intermediate wet well level can also be used.
Step 3
If the exit of the discharge piping is connected to a force main, enter the force main pressure (in feet) in cell D22. If
a range of pressures are expected, enter the average pressure. This value will be added to static pressure component
of the system curve.
Step 4
Calculate the head loss for all fittings and valves from the pump discharge to the discharge pipe outlet. Only fittings and
valves that are common to both pump flows should be entered twice. Individual fitting and valves should be accounted
for once. Add these values to the discharge pipe length and enter the sum, in total feet, into cell H22.
Step 5
Enter the friction losses (per 100' of pipe) due to flow in cells D25 - L25. The flow values, in red, directly above these cells will be
computed automatically and will be based upon the design flow of one pump.
Step 6
Click on the Analyzer tab to see the system curve. Mouse over the design point to see the system head that was
calculated at the design flow. Use these values to select a pump for evaluation.
Select a pump that you would like to analyze. If the flow points are are available in an excel compatable format
copy up to nine flow points and paste them into cells D28 through L28. Otherwise they must be entered manually.
Enter up to nine single pump flows in the yellow blocks beginning at cell D28. Select the units so that you can get
good coverage across the full range of flow. They have to begin with zero but fewer than nine can be used.
If you use fewer than nine, enter the last flow in the remanining cells. For example if Q7 is the last flow point,
enter its value in Q8 and Q9. If you leave them blank the graph will go crazy.
Step 7
Paste or enter the corresponding heads for each flow point in cells D29 - L29. If fewer that nine flow points were used,
enter the last actual value in the remaining cells per step 6.
Step 8
Enter the pump description into the yellow block at cell D31. This will be used as the title on the chart.
Step 9
Enter the pipe description into the yellow block at cell K31. This will be used as a side bar on the chart.
Step 10
Click on the Analyzer tab to evaluate the results.

## Notes
DESIGN NOTES
Subdivision Lift Station
Flows
400 homes with a per dwelling flow rate of 300 gpd -- Total flow 120000 gpd
Qin = (0.6 X 120000gpd) / 240min = 300 gpm
Qpump = Qin X 2 = 600 gpm
Pipe & Fittings
6" Steel sch 40 - 300'
Elbows (medium sweep) per pump - 3
Gate Valves per pump - 1
Check Valves per pump - 1
Tees per pump - 1
Elevation and Pressure
Max elevation from low level - 47' (min elevation 37' assumes 10' pump down)
Force main ave pressure - NA
Equivalent Pipe Length (Pipe friction based on Darcy's formula - Fitting equivalent length based on Foster's formula )
6" Pipe | 300
Elbows | 27
Gates | 5.7
Checks | 39
Tees | 10
Total | 381.7
Pump Selection