## Sheet1
SUBMERSIBLE MOTOR FLOW VELOCITY CALCULATOR
INPUT DATA
D1 Casing ID (inches) | 10 | 0.83333 | convert inches to feet
D2 Motor OD (inches) | 7.5 | 0.625 | convert inches to feet
Flow (GPM) | 1000 | 16.6667 | convert seconds to minutes
|  | 0 | convert PSI to feet
CALCULATED RESULTS |  | 0 | convert inches to feet
|  | 0 | convert inches to feet
Effective Flow Area (sqare inches) | 34.3612 |  | convert inches to feet
Effective Flow ID (inches) | 6.6144 | 1.784 | convert inches to gal / foot
Flow Velocity (ft/sec) | 9.3371 | 10.4107 | convert to pump down gallons
Friction Loss (per foot of motor length) | 0.040923
Notes:
Friction loss is in feet of water & assumes smooth steel (HW=140)
34.3612
6.6144
9.3371
0.040923
D1
D2