## VSPA
Variable Speed Performance Analyzer 60 Hertz with "Auto Plot"
Joe Evans, Ph.D 1/12/09
Follow the four steps below to view the potential power savings of a centrifugal pump operating under VFD control.
Scroll down to line 80 for more detailed instructions.
AFFINITY LAW CALCULATOR
[6 empty] | 1) Enter the chart title in yellow box # 1 | [6 empty] | 1 | Aurora 5X6X12 12" Trim 1750RPM
[6 empty] | Enter the flow units in yellow box # 2 | [6 empty] | 2 | Flow = M3/hr
[6 empty] | Enter the head units in yellow box # 3 | [6 empty] | 3 | Head = Meters
[6 empty] | Enter the power uints in yellow box # 4 | [6 empty] | 4 | Power = kw
| ENTER RPM IN CELL B22 |  |  |  |  | 2) Enter eight 60 hertz flows In Q1 - Q8 (Cells H22 - O22)
Enter the corresponding heads in H1 - H8 (Cells P22 - W22)
(*See instructions below when entering fewer than eight points)
[6 empty] | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8 | H1 | H2 | H3 | H4 | H5 | H6 | H7 | H8
60 | 3600 | 1 | 1 | 1 |  | 45.4 | 90.8 | 136.2 | 181.7 | 227.1 | 272.5 | 317.9 | 363.3 | 49.9 | 49.6 | 49 | 48.1 | 46.3 | 44.2 | 41.1 | 37.5
59 | 4248 | 0.98333 | 0.96694 | 0.95083 | 59 | 44.6433 | 89.2867 | 133.93 | 178.6717 | 223.315 | 267.9583 | 312.6017 | 357.245 | 48.2505 | 47.9604 | 47.3803 | 46.51 | 44.7695 | 42.7389 | 39.7414 | 36.2604 |  | Power Calculations
58 | 4176 | 0.96667 | 0.93444 | 0.9033 | 58 | 43.8867 | 87.7733 | 131.66 | 175.6433 | 219.53 | 263.4167 | 307.3033 | 351.19 | 46.6288 | 46.3484 | 45.7878 | 44.9468 | 43.2648 | 41.3024 | 38.4057 | 35.0417 | Q1 | Q2 | Q3 | Q4 | Q5 | Q6 | Q7 | Q8
57 | 4104 | 0.95 | 0.9025 | 0.85737 | 57 | 43.13 | 86.26 | 129.39 | 172.615 | 215.745 | 258.875 | 302.005 | 345.135 | 45.0347 | 44.764 | 44.2225 | 43.4102 | 41.7857 | 39.8905 | 37.0928 | 33.8438 | 17.6 | 22.3 | 25.9 | 30.8 | 34.4 | 39 | 42.8 | 48
56 | 4032 | 0.93333 | 0.87111 | 0.81304 | 56 | 42.3733 | 84.7467 | 127.12 | 169.5867 | 211.96 | 254.3333 | 296.7067 | 339.08 | 43.4684 | 43.2071 | 42.6844 | 41.9004 | 40.3324 | 38.5031 | 35.8027 | 32.6667
55 | 3960 | 0.91667 | 0.84028 | 0.77025 | 55 | 41.6167 | 83.2333 | 124.85 | 166.5583 | 208.175 | 249.7917 | 291.4083 | 333.025 | 41.9299 | 41.6778 | 41.1736 | 40.4174 | 38.9049 | 37.1403 | 34.5354 | 31.5104 | 13.5565 | 17.1767 | 19.9496 | 23.7238 | 26.4968 | 30.0399 | 32.9669 | 36.9722
54 | 3888 | 0.9 | 0.81 | 0.729 | 54 | 40.86 | 81.72 | 122.58 | 163.53 | 204.39 | 245.25 | 286.11 | 326.97 | 40.419 | 40.176 | 39.69 | 38.961 | 37.503 | 35.802 | 33.291 | 30.375
53 | 3816 | 0.88333 | 0.78028 | 0.68925 | 53 | 40.1033 | 80.2067 | 120.31 | 160.5017 | 200.605 | 240.7083 | 280.8117 | 320.915 | 38.9359 | 38.7018 | 38.2336 | 37.5314 | 36.1269 | 34.4883 | 32.0694 | 29.2604
52 | 3744 | 0.86667 | 0.75111 | 0.65096 | 52 | 39.3467 | 78.6933 | 118.04 | 157.4733 | 196.82 | 236.1667 | 275.5133 | 314.86 | 37.4804 | 37.2551 | 36.8044 | 36.1284 | 34.7764 | 33.1991 | 30.8707 | 28.1667
51 | 3672 | 0.85 | 0.7225 | 0.61412 | 51 | 38.59 | 77.18 | 115.77 | 154.445 | 193.035 | 231.625 | 270.215 | 308.805 | 36.0527 | 35.836 | 35.4025 | 34.7522 | 33.4517 | 31.9345 | 29.6947 | 27.0937
50 | 3600 | 0.83333 | 0.69444 | 0.5787 | 50 | 37.8333 | 75.6667 | 113.5 | 151.4167 | 189.25 | 227.0833 | 264.9167 | 302.75 | 34.6528 | 34.4444 | 34.0278 | 33.4028 | 32.1528 | 30.6944 | 28.5417 | 26.0417 | 10.1852 | 12.9051 | 14.9884 | 17.8241 | 19.9074 | 22.5694 | 24.7685 | 27.7778
49 | 3528 | 0.81667 | 0.66694 | 0.54467 | 49 | 37.0767 | 74.1533 | 111.23 | 148.3883 | 185.465 | 222.5417 | 259.6183 | 296.695 | 33.2805 | 33.0804 | 32.6803 | 32.08 | 30.8795 | 29.4789 | 27.4114 | 25.0104
48 | 3456 | 0.8 | 0.64 | 0.512 | 48 | 36.32 | 72.64 | 108.96 | 145.36 | 181.68 | 218 | 254.32 | 290.64 | 31.936 | 31.744 | 31.36 | 30.784 | 29.632 | 28.288 | 26.304 | 24
47 | 3384 | 0.78333 | 0.61361 | 0.48066 | 47 | 35.5633 | 71.1267 | 106.69 | 142.3317 | 177.895 | 213.4583 | 249.0217 | 284.585 | 30.6192 | 30.4351 | 30.0669 | 29.5147 | 28.4102 | 27.1216 | 25.2194 | 23.0104
46 | 3312 | 0.76667 | 0.58778 | 0.45063 | 46 | 34.8067 | 69.6133 | 104.42 | 139.3033 | 174.11 | 208.9167 | 243.7233 | 278.53 | 29.3301 | 29.1538 | 28.8011 | 28.2721 | 27.2141 | 25.9798 | 24.1577 | 22.0417
45 | 3240 | 0.75 | 0.5625 | 0.42188 | 45 | 34.05 | 68.1 | 102.15 | 136.275 | 170.325 | 204.375 | 238.425 | 272.475 | 28.0687 | 27.9 | 27.5625 | 27.0563 | 26.0437 | 24.8625 | 23.1188 | 21.0938 | 7.425 | 9.4078 | 10.9266 | 12.9938 | 14.5125 | 16.4531 | 18.0562 | 20.25
44 | 3168 | 0.73333 | 0.53778 | 0.39437 | 44 | 33.2933 | 66.5867 | 99.88 | 133.2467 | 166.54 | 199.8333 | 233.1267 | 266.42 | 26.8351 | 26.6738 | 26.3511 | 25.8671 | 24.8991 | 23.7698 | 22.1027 | 20.1667
43 | 3096 | 0.71667 | 0.51361 | 0.36809 | 43 | 32.5367 | 65.0733 | 97.61 | 130.2183 | 162.755 | 195.2917 | 227.8283 | 260.365 | 25.6292 | 25.4751 | 25.1669 | 24.7047 | 23.7802 | 22.7016 | 21.1094 | 19.2604
42 | 3024 | 0.7 | 0.49 | 0.343 | 42 | 31.78 | 63.56 | 95.34 | 127.19 | 158.97 | 190.75 | 222.53 | 254.31 | 24.451 | 24.304 | 24.01 | 23.569 | 22.687 | 21.658 | 20.139 | 18.375
41 | 2952 | 0.68333 | 0.46694 | 0.31908 | 41 | 31.0233 | 62.0467 | 93.07 | 124.1617 | 155.185 | 186.2083 | 217.2317 | 248.255 | 23.3005 | 23.1604 | 22.8803 | 22.46 | 21.6195 | 20.6389 | 19.1914 | 17.5104
40 | 2880 | 0.66667 | 0.44444 | 0.2963 | 40 | 30.2667 | 60.5333 | 90.8 | 121.1333 | 151.4 | 181.6667 | 211.9333 | 242.2 | 22.1778 | 22.0444 | 21.7778 | 21.3778 | 20.5778 | 19.6444 | 18.2667 | 16.6667 | 5.2148 | 6.6074 | 7.6741 | 9.1259 | 10.1926 | 11.5556 | 12.6815 | 14.2222
39 | 2808 | 0.65 | 0.4225 | 0.27463 | 39 | 29.51 | 59.02 | 88.53 | 118.105 | 147.615 | 177.125 | 206.635 | 236.145 | 21.0828 | 20.956 | 20.7025 | 20.3223 | 19.5617 | 18.6745 | 17.3648 | 15.8438
38 | 2736 | 0.63333 | 0.40111 | 0.25404 | 38 | 28.7533 | 57.5067 | 86.26 | 115.0767 | 143.83 | 172.5833 | 201.3367 | 230.09 | 20.0154 | 19.8951 | 19.6544 | 19.2934 | 18.5714 | 17.7291 | 16.4857 | 15.0417
37 | 2664 | 0.61667 | 0.38028 | 0.2345 | 37 | 27.9967 | 55.9933 | 83.99 | 112.0483 | 140.045 | 168.0417 | 196.0383 | 224.035 | 18.9759 | 18.8618 | 18.6336 | 18.2914 | 17.6069 | 16.8083 | 15.6294 | 14.2604
36 | 2592 | 0.6 | 0.36 | 0.216 | 36 | 27.24 | 54.48 | 81.72 | 109.02 | 136.26 | 163.5 | 190.74 | 217.98 | 17.964 | 17.856 | 17.64 | 17.316 | 16.668 | 15.912 | 14.796 | 13.5
35 | 2520 | 0.58333 | 0.34028 | 0.1985 | 35 | 26.4833 | 52.9667 | 79.45 | 105.9917 | 132.475 | 158.9583 | 185.4417 | 211.925 | 16.9799 | 16.8778 | 16.6736 | 16.3674 | 15.7549 | 15.0403 | 13.9854 | 12.7604 | 3.4935 | 4.4264 | 5.141 | 6.1137 | 6.8282 | 7.7413 | 8.4956 | 9.5278
34 | 2448 | 0.56667 | 0.32111 | 0.18196 | 34 | 25.7267 | 51.4533 | 77.18 | 102.9633 | 128.69 | 154.4167 | 180.1433 | 205.87 | 16.0234 | 15.9271 | 15.7344 | 15.4454 | 14.8674 | 14.1931 | 13.1977 | 12.0417
33 | 2376 | 0.55 | 0.3025 | 0.16638 | 33 | 24.97 | 49.94 | 74.91 | 99.935 | 124.905 | 149.875 | 174.845 | 199.815 | 15.0948 | 15.004 | 14.8225 | 14.5503 | 14.0058 | 13.3705 | 12.4328 | 11.3438
32 | 2304 | 0.53333 | 0.28444 | 0.1517 | 32 | 24.2133 | 48.4267 | 72.64 | 96.9067 | 121.12 | 145.3333 | 169.5467 | 193.76 | 14.1938 | 14.1084 | 13.9378 | 13.6818 | 13.1698 | 12.5724 | 11.6907 | 10.6667
31 | 2232 | 0.51667 | 0.26694 | 0.13792 | 31 | 23.4567 | 46.9133 | 70.37 | 93.8783 | 117.335 | 140.7917 | 164.2483 | 187.705 | 13.3205 | 13.2404 | 13.0803 | 12.84 | 12.3595 | 11.7989 | 10.9714 | 10.0104
30 | 2160 | 0.5 | 0.25 | 0.125 | 30 | 22.7 | 45.4 | 68.1 | 90.85 | 113.55 | 136.25 | 158.95 | 181.65 | 12.475 | 12.4 | 12.25 | 12.025 | 11.575 | 11.05 | 10.275 | 9.375 | 2.2 | 2.7875 | 3.2375 | 3.85 | 4.3 | 4.875 | 5.35 | 6
[7 empty] | 100 | 77 | 58
[14 empty] | 21.6017 | 21.4719 | 21.2121 | 20.8225 | 20.0433 | 19.1342 | 17.7922 | 16.2338
[14 empty] | 18.1515 | 18.0423 | 17.8241 | 17.4967 | 16.8419 | 16.078 | 14.9504 | 13.6409
[14 empty] | 15.0012 | 14.911 | 14.7306 | 14.4601 | 13.919 | 13.2876 | 12.3557 | 11.2734
[14 empty] | 12.151 | 12.0779 | 11.9318 | 11.7127 | 11.2744 | 10.763 | 10.0081 | 9.1315
[6 empty] | (*See instructions below when entering fewer than eight points) H1: 9.6008; (*See instructions below when entering fewer than eight points) H2: 9.543; (*See instructions below when entering fewer than eight points) H3: 9.4276; (*See instructions below when entering fewer than eight points) H4: 9.2544; (*See instructions below when entering fewer than eight points) H5: 8.9081; (*See instructions below when entering fewer than eight points) H6: 8.5041; (*See instructions below when entering fewer than eight points) H7: 7.9076; (*See instructions below when entering fewer than eight points) H8: 7.215 | [7 empty] | 0
[14 empty] | 7.3506 | 7.3064 | 7.218 | 7.0854 | 6.8203 | 6.5109 | 6.0543 | 5.524
[14 empty] | 5.4004 | 5.368 | 5.303 | 5.2056 | 5.0108 | 4.7835 | 4.4481 | 4.0584
[6 empty] | 3) To plot a constant or variable system curve, enter the | [7 empty] | SH1 | SH2 | SH3 | SH4 | SH5 | SH6 | SH7 | SH8
[6 empty] | system heads in SH1 - SH8 (Cells P64 - W64) that | [7 empty] | 22 | 22 | 23 | 25 | 29 | 36 | 45
| INSTRUCTIONS: | [12 empty] | 9.5238 | 9.5238 | 9.9567 | 10.8225 | 12.5541 | 15.5844 | 19.4805 | 0
correspond to the flows in Q1 - Q8. (See Instructions below)
[6 empty] | 4) Enter the pump's power requirements in P1 - P8 | [7 empty] | P 1 | P 2 | P 3 | P 4 | P 5 | P 6 | P 7 | P 8
[6 empty] | (Cells P70 - W70) that correspond to the flows in Q1 - Q8 | [7 empty] | 17.6 | 22.3 | 25.9 | 30.8 | 34.4 | 39 | 42.8 | 48
(See instructions below)
Click on the "VFD Control" tab to view pump performance.
| AFFINITY LAW CALCULATOR | [5 empty] | VSPA Instructions
The Variable Speed Performance Analyzer (VSPA) allows you to compare the operating frequency range of a given pump
to the system conditions it must match in various pumping applications.
Frequency and pump speed are synonymous, so the actual speed of the pump is not important. What is important is the
frequency (or speed) range. It is this range that dictates the potential power savings attainable by the application when
operating in a variable speed mode.
Step 1
Enter the chart title and units of measure as you would like them to appear on the chart. Any units of flow and head may
be used since power is calculated via the affinity laws.
Step 2
| Enter a motor speed for 60 Hz | [5 empty] | Auto Plot requires that you enter eight, 60 Hz operating points in the row with the yellow background. Flows are entered
| operation in the cell with the | [5 empty] | beneath Q1 - Q8 and the corresponding heads are entered beneath H1 - H8. It is not necessary to begin with shutoff head
| yellow background and motor | [5 empty] | unless the pump will operate to the far left of the curve. Corresponding flows and heads are calculated for each point from
| speeds at the lower frequencies | [5 empty] | 59 - 30 Hz, however, Auto Plot displays the curves in 5hz increments (i.e. 55, 50, 45, etc). The labels displayed at each
| will be displayed. Note that the | [5 empty] | xy intercept on the head / capacity curves is the power required at that point. *If you wish to enter fewer than eight points,
enter the last point multiple times. For example if you have only six points, enter the data in Q6/H6 again in both Q7/H7
and Q8/H8. The same will hold true for Steps 3 & 4.
Step 3
To generate a system curve, enter the system head for each flow point beneath SH1 - SH8.
Step 4
PPSA calculates the power required at each major flow point on each of the lower frequency cuves based on the values entered for 60hz
curve. Enter the power requirement for flows Q1 - Q8 beneath P1 - P 8. If Q1 is zero, leave P1 blank. Follow the instructions above for fewer
than eight points.
The Example
The example included is an Aurora 5X6X12 operating at 1750 RPM. The flow points entered are 45 - 363 M3/hr and the associated heads
are in meters. Power at each H/Q point is in kw. The system curve consists of both static and friction head.
Note also that the hydraulic efficiency of any flow / head point moves to the left as frequency and therefore pump speed is
reduced. The peak hydraulic efficiency of 84% occurs at 1200 M3/hr. This efficiency follows the H/Q isomer that is generated by the
by the lower frequency curves and migrates to the left as frequency (speed) is decreased. For example, the third H/Q point
from the right on each of the curves has an efficiency of 84%. The isomers generated by the other 60hz H/Q points also follow this rule.
http://www.pumped101.com